MundusLux-300

Stephenville Edition

Multi-Product Clean Energy Hub | Green Hydrogen & Ammonia | Desalination | Grid Services

Site: Long Point, Stephenville, NL | 48°42'23.86"N 58°53'26.70"W

Engineering Design Basis | Version 6.0 | January 2027

Design Maturity: 85% | Basis for Construction Bidding | Engineering Confidential

# Table of Contents

Right-click the TOC and select "Update Field" to refresh page numbers

Strategic Recommendations: Integrated Clean Energy Hub	3

Volume 6: Design Basis Memorandum	6

Volume 7: Process Design	8

Volume 8: Instrumentation & Control Systems	10

Volume 9: Safety Engineering — HAZOP Study	11

Volume 10: Structural & Electrical Engineering	12

Volume 11: Dynamic Operating Model	13

Volume 12: Capital Cost, Commissioning & Operations	14

Volume 13: Risk Analysis & Regulatory Compliance	15

Volume 14: Pilot-Scale Validation Plan	16

Volume 15: Technology Readiness Assessment	17

Volume 16: Indigenous & Community Engagement	18

Volume 17: Financing & Ownership Structure	19

Volume 18: Thermal Resilience & Winter Operations	20

Volume 19: Value Engineering & Cost Optimization	21

Volume 20: Zero-Carbon Thermal Strategy	22

Volume 21: Grid-Supportive Operations & Clean Grid Atlantic	23

Volume 22: Electrochemical Energy Systems & DAC	24

Volume 23: Green Hydrogen & Ammonia Production	25

Volume 24: Crown Land Wind Development Strategy	27

Appendices	28

Annex A: Profitable Standalone Operation Contingency	29

# Strategic Recommendations: Integrated Clean Energy Hub

The relocation of MundusLux-300 to Long Point, Stephenville, Newfoundland, represents a fundamental strategic pivot. The facility transforms from a California data-center-centric asset into a multi-product clean energy hub producing green hydrogen, green ammonia, and desalinated water, anchored by Newfoundland's world-class wind resources and the Port of Stephenville's ice-free deep-water infrastructure.

## Multi-Product Clean Energy Hub Pivot

Stephenville is the site of Project Nujio'qonik, Canada's first commercial green hydrogen and ammonia project. To ensure facility viability, MundusLux-300 produces green hydrogen and green ammonia alongside fresh water, leveraging the region's Class 7+ wind resources with average speeds of 7.2 m/s in winter and 5.32 m/s in summer. The facility operates as an integrated industrial load within the emerging Clean Grid Atlantic ecosystem.

## Partnership with World Energy GH2

World Energy GH2 holds leases on approximately 108,000 hectares of Crown land for wind farm development on the Port au Port Peninsula. The MundusLux-300 facility is designed for co-location with these wind assets, providing shared access to land, wind resource data, transmission corridors, and operational synergies. A formal Co-Location Agreement governs shared infrastructure, land use, and cost allocation.

## Port of Stephenville Integration

The facility's location at Long Point is in direct proximity to the Port of Stephenville, a year-round, ice-free deep-water port featuring 10-meter draft depth, a 72-meter wide entrance channel, 30-ton shore cranes, and extensive warehousing. The redesign includes a dedicated offshore offtake jetty for export of green ammonia and hydrogen carriers, plus equipment import via heavy-lift vessels. Port logistics integration is detailed in Volume 7.

## Port of Stephenville — Logistics Integration Plan

The facility leverages the Port of Stephenville's existing infrastructure for construction logistics, spare parts warehousing, and product export. Key logistics parameters:

| Parameter | Specification |
| --- | --- |
| Port type | Deep-water, ice-free, year-round |
| Channel depth | 10m at chart datum (12m at high tide) |
| Channel width | 72m entrance |
| Max vessel | 30,000 DWT NH3 carrier, 180m LOA |
| Shore cranes | 30-ton (existing) + 150-ton mobile (dedicated lease) |
| Warehouse space | 2,500 m² covered storage (leased from Port Authority) |
| Heavy equipment delivery | Wind turbine nacelles (80t), blades (15t x 75m), transformers (50t) via heavy-lift vessel |
| Spare parts inventory | 72-hour critical spares (BESS modules, membranes, compressor parts) |
| Product export — NH3 | 500 t/day loading rate; 18-20 vessel calls/year |
| Product export — LH2 | 20 t/day transfer; 8-10 vessel calls/year (pilot phase) |
| Emergency access | Helipad on facility; 5 min to Stephenville Hospital by air ambulance |

## Domestic Market Focus — Clean Grid Atlantic

The original European export model has been replaced by a domestic market strategy centered on Clean Grid Atlantic, the successor initiative developed by Pattern Energy and local stakeholders. The facility participates as: (1) a baseload industrial power consumer absorbing excess wind generation; (2) a grid stability provider offering frequency regulation and capacity reserves; and (3) a domestic green fuel producer serving Atlantic Canadian industrial demand.

## Revenue Model Restructuring

| Revenue Stream | Annual Value | Description |
| --- | --- | --- |
| Water Sales (Municipal/Industrial) | $1.2-2.5M | 50-130K GPD at $2.80-3.50/Kgal to Stephenville municipal & industrial users |
| Grid Export & Services | $1.8-3.5M | Surplus electricity sales + frequency regulation + capacity payments via Clean Grid Atlantic |
| Green Hydrogen Sales | $4.2-8.5M | Domestic industrial H2 at $3.50-5.00/kg, 2,000-3,500 kg/day from scaled PEM electrolysis |
| Green Ammonia Sales | $6.5-12M | Ammonia for fertilizer & maritime fuel at $650-850/tonne, 300-500 t/day |
| Grid Stability Contracts | $0.8-1.5M | Capacity + frequency regulation services to Newfoundland & Labrador Hydro |
| Clean Hydrogen ITC | $18-28M | Federal 40% Investment Tax Credit (construction-phase credit) |
| TOTAL STEADY-STATE | $32.5-56M/yr | Diversified revenue across five domestic streams |

## Power Purchase Agreement Framework

A 20-year Power Purchase Agreement (PPA) with Newfoundland and Labrador Hydro provides revenue certainty for the facility's dedicated 150 MW wind farm on Crown land. The PPA structure includes: baseload energy supply at $55/MWh (escalating at 2% annually); capacity payments of $12/kW-month; and renewable energy certificates transferable to the facility's hydrogen production for ITC carbon-intensity compliance. A Contract for Difference (CfD) floor price of $50/MWh de-risks the first 10 years of operation.

## Long-Term Crown Land Wind Development

The Port au Port Peninsula is one of the world's premier onshore wind resource regions, with World Energy GH2 already holding 4 GW of buildable wind capacity in provincial Crown land leases. MundusLux-300 secures a dedicated 150 MW wind farm allocation within this broader development, with expansion rights to 300 MW contingent on successful hydrogen market development. Crown land lease terms: $3,500/MW/year escalating at CPI; 30-year primary term with two 10-year renewal options.

# Volume 6: Design Basis Memorandum

Fundamental design parameters for MundusLux-300 Stephenville Edition. All deviations require written Engineering Manager approval.

## 6.1 Design Life & Availability

| Asset | Design Life | Replacement | Basis |
| --- | --- | --- | --- |
| Building structure | 50 yr | N/A | NBC 2020, Seismic Cat D, CSA S16 |
| PEM Electrolyzer stacks | 15 yr | 10-yr membrane refresh | CSA HGV 3.1, IEC 62282 |
| Ammonia synthesis loop | 25 yr | 15-yr catalyst | ASME BPVC VIII-1, CSA B51 |
| RO membranes | 7 yr | 5.5 yr | Mfr warranty + ice-resistant pre-treatment |
| MED tubes | 25 yr | N/A | Ti Grade 2, anti-scalant + freeze-protected |
| BESS LiFePO4 | 20 yr | 15-yr capacity refresh | 6,000 cycles, 80% DoD, -20C rated |
| Wind turbines (HAWT) | 25 yr | 10-yr gearbox | IEC 61400 Class I, cold-climate pkg |
| H2 storage (cryogenic) | 30 yr | 15-yr insulation vacuum | CSA HGV 3.1, ASME BPVC VIII-2 |
| NH3 storage tanks | 30 yr | N/A | API 620, double-wall, -33C design |

## 6.2 Availability Targets

| System | Target | Downtime/yr | Basis |
| --- | --- | --- | --- |
| PEM Electrolysis | 98.5% | 131 hr | 12-stack N+1, cold-weather pkg |
| Ammonia Synthesis | 96.0% | 350 hr | Haber-Bosch, 2-train N+1 |
| RO Desalination | 99.0% | 87.6 hr | 3-train N+1, heated intake |
| MED Desalination | 97.5% | 219 hr | N+1 vacuum, winterized |
| Thermal Storage | 99.9% | 8.8 hr | 5-tank 4+1, PCM freeze-protected |
| Wind Farm | 97.0% | 263 hr | IEC 61400, anti-icing system |
| Safety (SIS) | 99.99% | 0.9 hr | SIL-2/3 per IEC 61511 |
| Overall facility | 98.0% | 175 hr | Revenue-weighted |

## 6.3 Codes & Standards — Canadian Compliance

| Code | Edition | Application |
| --- | --- | --- |
| ASME BPVC VIII-1 | 2023 | Pressure vessels, HX, NH3 storage |
| CSA B51 / ASME B31.3 | 2022 | Process piping, H2 service |
| CSA HGV 3.1 | 2020 | Hydrogen generation & storage |
| API 650/620 | 13th/12th | Ammonia storage, cryogenic H2 |
| IEC 61511/62443 | 2016/2018 | SIS / Cybersecurity |
| NBC 2020 / CSA S16 / A23.3 | 2020 | Building, steel, concrete |
| CSA C22.1 Canadian Electrical Code | 2021 | Electrical systems |
| IEC 61400-1 | 2019 | Wind turbine design, cold climate |
| Newfoundland Water Resources Act (SNL2002 cW-4.01) | — | Water rights & discharge |
| CEAA 2012 / NREPA | — | Federal/provincial environmental assessment |

# Volume 7: Process Design

Process flow diagrams, equipment specifications, and pipe specifications for the integrated clean energy hub — hydrogen, ammonia, desalination, and grid services at Long Point, Stephenville.

## 7.1 Process Overview

[SEAWATER INTAKE] —> [Heated Traveling Screen] —> [RO Pre-treatment] —> [RO Trains] —> [IX Polish] —> [Product Water]

[WIND FARM 150 MW] —> [HV Substation] —> [PEM Electrolyzer 50 MW] —> [H2 Compression] —> [Cryogenic H2 Storage] —> [Ammonia Synthesis] —> [NH3 Storage] —> [Offtake Jetty]

[WIND FARM 150 MW] —> [HV Substation] —> [Facility Load] / [Grid Export] / [BESS Charging] —> [Grid Services Controller]

[GPU RACKS] —> [PCM Buffer] —> [MED Thermal Feed] / [District Heat Export] —> [MED 6-Effect] —> [Distillate]

## 7.2 Equipment Specifications

| Equipment | Tag | Specification | Duty |
| --- | --- | --- | --- |
| PEM Electrolyzer Bank A | EL-101 | 25 MW PEM, 5,000 Nm³/h H2 | Wind power —> green hydrogen |
| PEM Electrolyzer Bank B | EL-102 | 25 MW PEM, 5,000 Nm³/h H2 | Redundant bank for 98.5% availability |
| H2 Compressor | CP-201 | 3-stage, 30 to 350 bar | Feedstock compression for NH3 synthesis |
| Ammonia Synthesis Converter | NH-301 | Haber-Bosch, 300 t/day | H2 + N2 —> NH3 via promoted Fe catalyst |
| NH3 Storage Tank T-1 | TK-401 | Double-wall, 5,000 m³ | -33°C liquid ammonia storage |
| Cryogenic H2 Storage | TK-501 | Vacuum-insulated, 200 t | -253°C liquid H2, 30-day buffer |
| RO Train A/B/C | RO-101/2/3 | SWRO, 80K GPD each | Seawater —> permeate, heated intake |
| MED Unit | MED-301 | 6-effect, Ti tubes | 160K GPD distillate, winterized |
| PCM Buffer | TES-401 | 180 m³, Al-foam enhanced | 240-min thermal protection, freeze-protected |
| Thermal Storage | TES-402 | 750K gal stratified | Diurnal + seasonal load matching |
| Wind Turbine (x30) | WT-101-130 | 5 MW HAWT, cold-climate | IEC 61400 Class I, anti-icing |
| MVC Concentrator | MVC-501 | 800 kW electric | Brine ZLD, salt-to-power feed |

## 7.3 Pipe Specifications — Winterized for Newfoundland

| Line | Size | Material | Service | Temp/Press | Winterization |
| --- | --- | --- | --- | --- | --- |
| SW-101 | 16in | Super Duplex 2507 | Seawater intake | -2°C / 2 bar | Heated intake, 2kW trace |
| H2-201 | 12in | 316L SS (H2 service) | Hydrogen product | -40°C / 350 bar | Vacuum-insulated, H2-rated |
| NH-301 | 10in | Carbon steel + cladding | Ammonia product | -33°C / 18 bar | Double-wall insulation |
| RO-201 | 8in | 316L SS | RO permeate | 5°C / 2 bar | 20mm ArmaFlex insulation |
| RO-202 | 10in | Super Duplex 2507 | RO concentrate | -2°C / 58 bar | Heated by waste heat loop |
| MED-301 | 12in | Ti Grade 2 | MED feed | 52°C / 1.5 bar | 30mm mineral wool + Al jacket |
| CL-501 | 8in | HDPE DC PN16 SDR11 | GPU/Compute coolant | 55°C / 10 bar | Heated trace, glycol backup |
| FW-601 | 8in | HDPE PE100 | Freshwater distrib. | 5°C / 4 bar | Buried below frost line (1.5m) |
| BR-702 | 6in | FRP + heated liner | Brine to crystallizer | 35°C / 1 bar | Heated diffuser, 1kW trace |

## 7.4 Seawater Intake — Anti-Icing Design

The seawater intake at Long Point operates year-round in water temperatures ranging from -1.8°C (winter) to 12°C (summer). The intake structure includes: a subsurface velocity cap intake at 8m depth below lowest normal tide; a 2 kW electric trace heating system on the intake screen; a 5% glycol injection system for screen anti-freeze; and a heated traveling screen (0.5 kW/m²) to prevent ice accumulation. The intake channel is dredged to 10m depth with 2m cover below lowest astronomical tide.

# Volume 8: Instrumentation & Control Systems

168 instrument tags across 16 safety instrumented functions (SIFs). ISA S5.1 nomenclature. IEC 62443 SL-2 cybersecurity. Winterized instrumentation package included.

## 8.1 Instrument Count by Type

| Type | Count | Key Applications |
| --- | --- | --- |
| Temperature (RTD/Thermocouple) | 52 | Electrolyzer stacks, PCM buffer, MED effects, H2 storage, ambient |
| Pressure | 36 | H2 compression (350 bar), NH3 storage, RO high-pressure |
| Flow (magnetic/Coriolis/ultrasonic) | 32 | Seawater, H2 product, NH3 product, brine, coolant |
| Level (radar/dp) | 22 | Storage tanks, MED effects, NH3 tanks, cryo H2 |
| H2 / NH3 / Gas detection | 14 | H2 leak (0-100% LEL), NH3 leak (0-500 ppm), O2 depletion |
| Vibration | 8 | Electrolyzer compressors, wind turbine gearboxes |
| Ice / Weather | 4 | Intake ice detection, anemometer, ambient temp |

## 8.2 Winterized Instrumentation Package

All field instruments are specified with cold-climate packages rated to -40°C ambient: heated instrument enclosures (50W, thermostatically controlled); silicone-filled pressure transmitters (no oil freezing); and armored signal cables with UV/cold-rated jacketing (CSA C22.2 No. 174). The DCS cabinet HVAC maintains 15-25°C internal temperature via a 5 kW resistive heater with redundant thermostat. A dedicated Winter Operations SCADA panel provides real-time ice monitoring, heated equipment status, and automated winter shutdown sequencing.

# Volume 9: Safety Engineering — HAZOP Study

HAZOP per IEC 61882 with 8 nodes, 40 deviations, and 12 action items. FMEA per MIL-STD-1629A. Winter-specific hazards included.

## 9.1 HAZOP Nodes

| Node | Description | Deviations | Actions |
| --- | --- | --- | --- |
| PEM Electrolyzer Bank | 25 MW, 80°C, 30 bar differential | Overtemp, overpressure, H2 leak, power loss | 4 actions: H2 detection SIL-3, emergency vent, nitrogen purge, cold-weather drain |
| H2 Compression & Storage | 350 bar, -253°C cryo, 200 t | Leak, embrittlement, boil-off, vacuum loss | 3 actions: H2 detection SIL-3, emergency vent stack, passive vacuum monitoring |
| NH3 Synthesis & Storage | Haber-Bosch, -33°C, 18 bar | Leak, catalyst failure, overpressure | 2 actions: NH3 detection + water spray, pressure relief to scrubber |
| MED thermal feed | 6-effect, 58°C, 1.5 bar | Low temp, vacuum loss, brine leak, freeze | 2 actions: TMI controller, PCM backup, glycol trace heating |
| RO high-pressure | 58 bar, 240K GPD | Overpressure, membrane rupture, ice blockage | 1 action: relief valves + pressure trip + heated intake |
| Brine handling | 165 ppt, ZLD | Overflow, crystallizer failure, ice plug | 1 action: secondary containment + heated discharge diffuser |
| Wind turbine (ice throw) | 5 MW, 150m rotor, -20°C | Ice throw, blade icing, gearbox overtemp | 1 action: ice detection auto-shut, 500m exclusion zone |
| Grid islanding / BESS | 50 MWh BESS, 150 MW wind | Frequency excursion, arc flash, thermal runaway | 1 action: MGC controller + arc flash PPE + BMS thermal management |

# Volume 10: Structural & Electrical Engineering

## 10.1 Structural Design — Winterized for Newfoundland

| Parameter | Value | Code / Basis |
| --- | --- | --- |
| Seismic design | NBC 2020, Site Class C, Ss=0.45g | NBCC Seismic Hazard, low seismicity |
| Wind load | 170 km/h 3-sec gust (design) | NBC 2020 + 20% gust factor for Long Point exposure |
| Snow load | 3.5 kPa ground snow | NBC 2020, Stephenville zone, 1-in-50 year |
| Ice load | 1.0 kPa radial ice | CSA S37, Newfoundland coastal icing |
| Foundation | Drilled piers, 15-25m depth | Geotechnical SOW, bedrock at 12-18m |
| Building envelope | R-40 walls, R-60 roof, triple-glazed | NECB 2020, freeze-thaw resistant |
| Heated floor slab | Hydronic radiant, 50 W/m² | Prevents ground heave, maintains 5°C minimum |
| Building footprint | 30,000 sq ft H2/NH3 + 20,000 sq ft desal + 10,000 sq ft control | Phase 1 buildout |

## 10.2 Electrical Single-Line

66 kV utility interconnection —> 150 MVA main transformer —> 13.8 kV switchgear. On-site generation: 150 MW wind farm (30 x 5 MW), 50 MW PEM electrolyzer load, 50 MWh BESS (LiFePO4, cold-climate rated), 5 MW diesel backup. HV DC-coupled 1500V bus for electrolyzer banks. Grid connection via Clean Grid Atlantic 230 kV transmission corridor.

## 10.3 Protection Coordination

| Device | Rating | Setting | CT Ratio |
| --- | --- | --- | --- |
| Utility relay (66 kV) | 25 kA interrupt | 51V, 67N, 79, 87T | 1200:5 |
| Main breaker | 31.5 kA | LSIG, ZSI | — |
| BESS breaker | 8 kA | 51, 27/59, 81O/U, 86 | 2000:5 |
| Wind farm breaker | 12 kA | 51, 67, 81O/U | 1200:5 |
| Electrolyzer breaker | 6 kA | 51, 50/27, arc flash | 800:5 |

# Volume 11: Dynamic Operating Model

Three representative days with hourly thermal and electrical balances for Stephenville climate.

## 11.1 Winter Peak Wind Day (January 15)

| Hour | Wind Gen | Electrolyzer | NH3 Synth | Facility Load | BESS | Grid Export | MED Output |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 02:00 | 95 MW | 45 MW | 25 MW | 8 MW | +12 MW | +5 MW | 160K GPD |
| 06:00 | 88 MW | 42 MW | 25 MW | 8 MW | +8 MW | +5 MW | 160K GPD |
| 10:00 | 82 MW | 40 MW | 25 MW | 8 MW | +5 MW | +4 MW | 155K GPD |
| 14:00 | 78 MW | 38 MW | 25 MW | 8 MW | +3 MW | +4 MW | 152K GPD |
| 18:00 | 90 MW | 43 MW | 25 MW | 8 MW | +10 MW | +4 MW | 158K GPD |
| 22:00 | 98 MW | 47 MW | 25 MW | 8 MW | +13 MW | +5 MW | 160K GPD |

## 11.2 Summer Moderate Day (July 15)

| Hour | Wind Gen | Electrolyzer | NH3 Synth | Facility Load | BESS | Grid Export | MED Output |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 06:00 | 35 MW | 15 MW | 15 MW | 8 MW | -3 MW | 0 | 140K GPD |
| 10:00 | 28 MW | 12 MW | 10 MW | 8 MW | -2 MW | 0 | 148K GPD |
| 14:00 | 22 MW | 10 MW | 10 MW | 8 MW | 0 | -6 MW | 152K GPD |
| 18:00 | 30 MW | 14 MW | 15 MW | 8 MW | -4 MW | -11 MW | 145K GPD |
| 22:00 | 42 MW | 18 MW | 20 MW | 8 MW | -4 MW | 0 | 155K GPD |

## 11.3 Low Wind / Islanding Day (0% Grid)

| Hour | Wind Gen | Electrolyzer | NH3 Synth | Facility Load | BESS Discharge | Diesel | MED Output |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 06:00 | 12 MW | 5 MW | 5 MW | 8 MW | +8 MW | 0 | 120K GPD |
| 10:00 | 8 MW | 3 MW | 3 MW | 8 MW | +10 MW | 0 | 130K GPD |
| 14:00 | 5 MW | 2 MW | 2 MW | 8 MW | +12 MW | 0 | 135K GPD |
| 18:00 | 15 MW | 6 MW | 6 MW | 8 MW | +5 MW | 0 | 140K GPD |
| 22:00 | 20 MW | 8 MW | 8 MW | 8 MW | +2 MW | 0 | 145K GPD |

At 0% grid availability, the 50 MWh BESS provides 12+ hours of full facility operation at reduced electrolyzer output. The diesel generator (5 MW) provides emergency backup for critical safety and control systems only.

# Volume 12: Capital Cost, Commissioning & Operations

## 12.1 Capital Cost Estimate

| Item | CAPEX ($M) | Notes |
| --- | --- | --- |
| Wind farm (30 x 5 MW, cold-climate) | $285.0 | Turbines, foundations, 66kV collection, access roads |
| PEM electrolyzer (50 MW, 2 banks) | $62.5 | EL-101/102, transformers, water purification feed |
| Ammonia synthesis (300 t/day) | $48.0 | Haber-Bosch, air separation, catalyst, refrigeration |
| H2 storage (200 t cryogenic) | $28.0 | Vacuum-insulated tanks, BOG management |
| NH3 storage (5,000 m³) | $18.0 | Double-wall, refrigeration, loading arms |
| RO desalination (3-train) | $42.0 | Heated intake, membrane trains, energy recovery |
| MED desalination (winterized) | $38.0 | 6-effect Ti, PCM buffer, glycol trace heating |
| Brine management (heated outfall) | $12.0 | Heated FRP diffuser, ZLD crystallizer |
| BESS (50 MWh LiFePO4, cold-climate) | $22.0 | Containerized, HVAC heating, BMS |
| Grid interconnection (66 kV) | $15.0 | Switchyard, transformer, 10 km line to POI |
| Building & civil (winterized envelope) | $18.0 | R-40/R-60, heated slab, snow/ice rated |
| Offtake jetty & port logistics | $14.0 | Deep-water berth, NH3/H2 loading, port cranes |
| Instrumentation & SCADA (winterized) | $9.5 | Heated enclosures, winter ops panel, H2/NH3 detection |
| Zero-carbon thermal + geothermal study | $8.5 | Geothermal exploration ($2.8M), solar thermal, PCM |
| Grid services + Clean Grid Atlantic integration | $6.5 | AGC controller, metering, communications |
| Salt-to-power + DAC systems | $5.5 | SGE + MCDI, saltwater battery, DAC pilot |
| SUBTOTAL | $632.5 |  |
| Contingency (15%) | $94.9 | Winter construction + technology integration risk |
| TOTAL PROJECT COST | $727.4 | Includes all winterization and hydrogen/ammonia systems |

## 12.2 Commissioning Phases

18-phase commissioning over 24 months: Phase 1 (civil/structural, incl. heated foundations); Phase 2-5 (wind farm erection + grid connection); Phase 6-8 (H2/NH3 mechanical systems); Phase 9-11 (desalination wet testing, winterized); Phase 12 (electrolyzer bank A commissioning); Phase 13 (electrolyzer bank B + performance testing); Phase 14 (ammonia synthesis catalyst activation); Phase 15 (BESS + microgrid islanding); Phase 16 (grid services + Clean Grid Atlantic integration); Phase 17 (salt-to-power + DAC pilot); Phase 18 (performance guarantee + 168-hour reliability run in winter conditions).

## 12.3 O&M Summary

| Category | Annual Cost | Notes |
| --- | --- | --- |
| Labor (25 FTE, lean + automated) | $3.2M | Remote ops capable, local hiring preference 60% |
| Wind farm O&M (cold-climate) | $4.5M | Anti-icing, gearbox service, blade repair, 1.6% of CAPEX |
| Electricity (net, post-PPA) | $0.8M | Net after wind self-generation + grid export revenue |
| Electrolyzer maintenance | $1.8M | Membrane refresh, stack replacement reserve, deionized water |
| Ammonia synthesis O&M | $1.2M | Catalyst, compression, refrigeration, loading |
| Chemicals (desalination) | $0.22M | 90% reduction via FO pre-treatment |
| Insurance | $5.5M | $285M wind + $200M H2/NH3 + $50M BI |
| Maintenance & spare parts | $3.8M | Cold-climate spare inventory, 72-hr access via Port of Stephenville |
| Winter operations premium | $0.8M | Heating, de-icing, snow removal, winter PPE |
| TOTAL OPEX | $21.9M | Fully loaded steady-state operations |

# Volume 13: Risk Analysis & Regulatory Compliance

## 13.1 Permit Matrix — Newfoundland & Federal

| Permit / Authorization | Agency | Timeline | Status | Risk |
| --- | --- | --- | --- | --- |
| Environmental Assessment (EA) | NLDECCA / IAAC (CEAA 2012) | 18-24 mo | Required | Medium — follow Nujio'qonik EIS precedent |
| Water Use Licence | NLDECCA (WR Act) | 6-12 mo | Required | Medium — Crown owns water, industrial priority |
| Wastewater Discharge Permit | NLDECCA | 6-9 mo | Required | Low — heated diffuser, 100:1 dilution |
| Crown Land Lease (wind) | NLNR | 12-18 mo | Required | Medium — co-location with WE GH2 reduces risk |
| Building Permit | Town of Stephenville | 3-6 mo | Required | Low — NBC 2020 compliant |
| H2/NH3 Storage & Handling | NLLPS / C-NLOPB | 9-12 mo | Required | Medium — CSA HGV 3.1, PSM |
| Grid Interconnection | NLH / PUB | 12-18 mo | Required | Medium — Clean Grid Atlantic alignment |
| Clean Hydrogen ITC Registration | CRA | 3-6 mo post-FID | Required | Low — 40% credit, ITC legislation enacted |
| Qalipu First Nation Consultation | Qalipu FN / NL IRR | Ongoing | Required | Medium — robust IBA required |
| Navigable Waters / Jetty | DFO / CCG | 6-9 mo | Required | Low — Port of Stephenville coordination |

## 13.2 Regulatory Strategy

The Labrador Inuit Land Claims Agreement Act (SNL2004 cL-3.1) applies to the Labrador Inuit Settlement Area. While Long Point, Stephenville, is outside the Settlement Area on the island of Newfoundland, the project will consult the Nunatsiavut Government on any trans-shipment activities through Labrador ports and respect the principles of the Agreement in all dealings with Indigenous communities. The Newfoundland Water Resources Act (SNL2002 cW-4.01) governs all water rights: property and right to use water are vested in the Crown (s.9). Water use licences are required for industrial purposes, with priority given to domestic, then municipal, then agricultural, then commercial/industrial purposes (s.15). The facility will apply for an industrial water use licence under s.14, supported by an environmental assessment demonstrating no adverse effects on downstream water quality or aquatic habitat.

## 13.3 Environmental Assessment Strategy

Given the project scale (150 MW wind farm, 50 MW PEM electrolyzer, 300 t/day ammonia synthesis, marine offtake jetty), a comprehensive federal Environmental Assessment under CEAA 2012 and provincial assessment under NREPA is required. The EA process follows the Nujio'qonik EIS precedent and is structured in four phases:

| Phase | Timeline | Activities | Key Deliverables |
| --- | --- | --- | --- |
| Phase 1: Pre-Application Consultation | Months 1-6 | Early engagement with IAAC, NLDECCA, DFO, CCG, Qalipu FN, Nunatsiavut Government; scope refinement; technical working groups established | Project description, EA scope agreement, Indigenous consultation plan |
| Phase 2: EIS Preparation | Months 7-18 | 12-month study period: oceanography (currents, stratification, ice), air quality (H2/NH3 dispersion modelling), noise (wind turbines, compressors), wildlife (migratory birds, marine mammals, caribou), socio-economic (employment, community services), GHG lifecycle assessment | Draft EIS: 15 technical chapters, cumulative effects assessment, climate change resilience |
| Phase 3: Public Participation | Months 13-18 (concurrent) | Open houses in Stephenville, Port au Port, Corner Brook; technical review committee with Qalipu FN representatives; online portal; 30-day public comment period on draft EIS | Public consultation record, Indigenous knowledge integration, feedback responses |
| Phase 4: Decision & Conditions | Months 19-24 | Ministerial review, EA certificate issuance with legally binding conditions (monitoring, mitigation, adaptive management), water use licence issuance post-EA approval | EA Certificate, water use licence, Crown land lease activation |

Total timeline from project description to EA certificate: 24-30 months. Construction start is gated on EA certificate issuance, Qalipu First Nation IBA execution, and Crown land lease finalization. A dedicated EA Manager coordinates all submissions with a $4.5M budget for consultant studies, community engagement, and regulatory fees.

# Volume 14: Pilot-Scale Validation Plan

$24.5M, 5% scale, 30-month program with go/no-go gates at Month 6, 12, 18, and 24. Extended timeline accounts for winter validation requirements.

## 14.1 Pilot Modules

| Module | Scale | Cost | Duration |
| --- | --- | --- | --- |
| PEM electrolyzer pilot | 250 kW, 50 Nm³/h H2 | $4.2M | Months 1-8 |
| Ammonia synthesis pilot | 3 t/day Haber-Bosch | $3.8M | Months 4-12 |
| RO desalination (winterized) | 8K GPD | $2.5M | Months 1-6 |
| MED thermal (winterized) | 8K GPD | $3.5M | Months 3-9 |
| Cold-climate wind turbine | 1 x 100 kW | $1.8M | Months 1-10 |
| PCM buffer (freeze-protected) | 3.6 m³ | $1.4M | Months 4-8 |
| Heated seawater intake | Full-scale section | $2.1M | Months 1-6 |
| SGE + MCDI + DAC pilot | 5 m² RED + 50 kg CO2/day DAC | $2.0M | Months 14-24 |
| Saltwater flow battery | 10 kW / 50 kWh | $0.8M | Months 16-24 |
| Winter operations automation | Full SCADA integration | $1.4M | Months 12-24 |
| Go/No-Go Gates | — | $1.0M | Months 6, 12, 18, 24 |

# Volume 15: Technology Readiness Assessment

NASA TRL scale assessment of 16 subsystems. Three subsystems on critical path below TRL 7.

| Subsystem | TRL | Risk | Path to TRL 9 |
| --- | --- | --- | --- |
| PEM Electrolyzer (50 MW scale) | 8 | Low | Proven at 20 MW; scale-up validated via pilot |
| Haber-Bosch NH3 synthesis (300 t/day) | 9 | Low | Mature technology, cold-climate adaptation only |
| Cryogenic H2 storage (200 t) | 7 | Medium | Pilot validates BOG management + vacuum integrity |
| Cold-climate wind turbine (5 MW) | 9 | Low | Commercially available, Vestas/Siemens cold-climate pkg |
| Heated seawater intake | 7 | Medium | Pilot validates anti-icing under -2°C conditions |
| RO desalination (winterized 58 bar) | 9 | Low | Proven technology, heated intake is only delta |
| MED 6-effect (low temp, winterized) | 8 | Low | Pilot validates glycol trace + freeze protection |
| PCM buffer (freeze-protected) | 7 | Medium | Pilot Month 4-8, subcooling prevention design |
| Grid services + Clean Grid Atlantic AGC | 7 | Medium | Code integration + NLH interop testing |
| DAC pilot (solid sorbent) | 6 | Medium-High | TRL 6 pilot, scale-up to TRL 8 by Year 3 |

# Volume 16: Indigenous & Community Engagement Plan

12 stakeholder groups, 48-month timeline, $3.2M budget. Key groups: Qalipu First Nation (primary Indigenous rights holder), Nunatsiavut Government (consultation on trans-shipment), Town of Stephenville, Port of Stephenville Authority, local fishermen's association, Acadian Federation of Newfoundland, environmental coalitions, and provincial/federal agencies.

## 16.1 Indigenous Engagement — Qalipu First Nation

The Qalipu First Nation represents Mi'kmaq people of the west coast of Newfoundland, including the Stephenville and Port au Port region. An Impacts and Benefits Agreement (IBA) with the Qalipu First Nation is a condition precedent to financial close. The IBA will address: employment and training targets (minimum 15% Qalipu employment during construction, 10% during operations); business contracting opportunities; cultural heritage protection; environmental monitoring participation; and a community benefit fund of $150,000/year for education and cultural programs. Consultation follows the Crown's duty to consult and accommodate, coordinated through NL Department of Indigenous Relations and Reconciliation.

### IBA Progress Status

The Impacts and Benefits Agreement with the Qalipu First Nation is currently in the DRAFTING phase (as of January 2027). Milestones achieved: Preliminary consultation completed (Month 1-6); Cultural heritage baseline survey initiated; Draft IBA terms circulated for Qalipu Band Council review; and Environmental assessment consultation protocol agreed. Outstanding items: Final employment target negotiation (project seeks 12% Qalipu operations employment, Band Council seeking 18%); community benefit fund governance structure; and business contracting set-aside percentages. Expected IBA execution: Month 14-16 of the development timeline, gated on EA scope agreement. If IBA is not executed by Month 18, the Crown land lease cannot be activated and project FID is delayed.

## 16.2 Community Commitments

| Commitment | Value | Timeline |
| --- | --- | --- |
| Local hiring preference (Stephenville area) | 60% of 25 FTE from NL West Coast | Year 1 |
| Qalipu First Nation employment target | 10% operations, 15% construction | Year 1 |
| Water surplus for community | 50K GPD at cost to municipal district | Year 2 |
| Emergency water reserve | 1.5M gal winter-secure storage | Year 1 |
| Marine monitoring program | $150K/yr independent monitoring | Ongoing |
| Education & visitor center | Green energy education facility | Year 3 |
| Community benefit fund (Qalipu) | $150K/yr | Year 1 ongoing |
| Apprenticeship & training program | 5 positions/year, MUN Grenfell partnership | Year 1 |

# Volume 17: Financing & Ownership Structure

$727.4M capital stack (v6.0 Stephenville Edition), structured to maximize Canadian clean energy incentives and de-risk through diversified revenue streams.

## 17.1 Capital Stack

| Source | Amount ($M) | Terms | Return |
| --- | --- | --- | --- |
| Senior debt (project finance) | $320 | 7.0% fixed, 18-yr | 1.6x MOIC |
| Clean Hydrogen ITC (40%) | $145 | Refundable tax credit, Year 2-3 | N/A — non-dilutive |
| Clean Technology ITC (wind, 30%) | $85.5 | Refundable tax credit, Year 2-3 | N/A — non-dilutive |
| Provincial green bond (NLDC) | $75 | 5.5% tax-exempt, 20-yr | 1.5x MOIC |
| Strategic partner (World Energy GH2) | $45 | 18% equity | 5.2x MOIC |
| Management / sponsor equity | $25 | Sweat equity | 8.5x MOIC |
| Provincial development fund (ACOA) | $20 | 2.0% concessional, 25-yr | 1.2x MOIC |
| SGIP + ITC + provincial rebates | $11.9 | Upfront credits | N/A |
| TOTAL | $727.4 | — | — |

## 17.2 Cash Flow Summary

| Year | Revenue ($M) | OpEx ($M) | Debt Service ($M) | Net CF ($M) |
| --- | --- | --- | --- | --- |
| 1-2 (construction) | $0 | $3.5 | $0 | -$3.5 |
| 3 (ramp) | $28 | $14.5 | $32.0 | -$18.5 |
| 5 (steady-state) | $48 | $21.9 | $32.0 | -$5.9 |
| 7 (H2 market mature) | $72 | $21.9 | $28.0 | $22.1 |
| 10 (debt-free) | $85 | $22.5 | $0 | $62.5 |
| 15 (expansion) | $120 | $26.0 | $0 | $94.0 |

## 17.3 Federal Clean Hydrogen Tax Credit Strategy

The facility qualifies for the maximum 40% Clean Hydrogen Investment Tax Credit by producing hydrogen via PEM electrolysis powered by new wind generation, achieving a carbon intensity below 0.5 kg CO2e/kg H2 (well below the 2.0 kg threshold for the 40% tier). The ITC applies to eligible property costs for electrolyzer stacks, wind turbines, and grid interconnection equipment acquired and available for use before 2035. Labour requirements (prevailing wages + apprenticeship quotas) are met through the project's collective agreement with the Newfoundland Building Trades and the apprenticeship partnership with Memorial University Grenfell Campus. The Contract for Difference (CfD) with the federal government provides a guaranteed carbon credit floor price of $85/tCO2e, backstopping revenue from the federal OBPS and provincial carbon pricing systems.

# Volume 18: Thermal Resilience & Winter Operations

Four-intervention system eliminates thermal cascade stall risk and ensures year-round operation in Stephenville's sub-freezing climate. This is the facility's single most critical operational vulnerability.

## 18.1 Threat Analysis — Newfoundland Winter

| Scenario | Temp Drop Rate | Time to Stall | Consequence |
| --- | --- | --- | --- |
| Full GPU rack outage (25%) | -8°C / 3 min | 15-20 min | MED vacuum break, 4-hr restart, pipe freeze risk |
| Scheduled maintenance (50%) | -4°C / 5 min | 20-30 min | Reduced output, geothermal backup ramp |
| Wind farm low output (0%) | -12°C / 5 min | 10-15 min | Electrolyzer trip, NH3 synth H2 starvation |
| Cooling pump failure (N) | -10°C / 5 min | 8-12 min | Full MED trip, emergency glycol circulation |
| Intake ice blockage | N/A — flow reduction | 30-60 min | RO trip, heated screen activation |

## 18.2 PCM Thermal Buffer — Freeze-Protected

180 m³ tank with 3D-printed Al foam inserts (20x conductivity boost) and dimethyl terephthalate PCM (67°C phase change, 165 kJ/kg). The higher phase change temperature provides greater thermal headroom above the glycol anti-freeze setpoint of -15°C. A subcooling prevention system monitors PCM temperature and triggers electric heating (50 kW) if temperature approaches 5°C above freeze point. Total latent heat capacity: 19,800 kWh, providing 240 minutes of passive protection at full MED load.

## 18.3 Geothermal Backup Heat Source

A $2.8M slim-hole geothermal exploration well (Month 8-12 of pilot) targets 85°C water at 800m depth, with expected flow of 25 L/s and 1.5 MW thermal output. If confirmed, a $8.5M production well pair provides 24/7 baseload heat independent of wind, solar, or GPU load — critical for winter survival mode. The geothermal system connects to the thermal distribution loop via a plate heat exchanger and operates in priority below GPU waste heat but above the electric MVC compressor. Expected capacity factor: 95%. Expected thermal output: 1.5 MW at 85°C. If the geothermal resource proves insufficient at Long Point, a connection to the provincial grid via the Clean Grid Atlantic 230 kV corridor provides firm backup heating via a 3 MW electric resistance boiler.

## 18.4 Enhanced Glycol Trace Heating

All process piping, seawater intake, brine outfall, and instrument lines are protected by a closed-loop glycol trace heating system (35% propylene glycol, -15°C freeze point). Key specifications: 20 W/m linear heat trace on process lines; 50 W/m on seawater intake and brine discharge; 0.5 kW/m² on valve stations and instrument enclosures; and a 500 kW central glycol heater with N+1 redundancy. The system operates automatically when ambient temperature falls below 2°C, with SCADA monitoring of all trace zones. Annual energy consumption: 2,200 MWh at $0.055/kWh (wind PPA rate) = $121,000/year.

## 18.5 Winterized Brine Discharge

The brine discharge system uses Super Duplex 2507 pipe (replaced from FRP for ice impact resistance) with a heated multiport diffuser. The diffuser maintains discharge temperature above 5°C through inline electric heating (100 kW) to prevent ice formation at the discharge point. Discharge depth: 15m below lowest tide, 200m offshore. The 100:1 dilution target is maintained even under winter stratification conditions. Marine impact monitoring includes quarterly benthic surveys and continuous temperature logging.

## 18.6 Summary — Winter Resilience

| Intervention | CAPEX | Net Annual OpEx | Key Benefit |
| --- | --- | --- | --- |
| PCM Thermal Buffer (freeze-protected) | $1.8M | $42K | 240-min passive protection, -40°C rated |
| Geothermal exploration + production | $11.3M | $12K | 1.5 MW 24/7 baseload heat, grid-independent |
| Glycol trace heating system | $2.4M | $121K | Complete freeze protection all piping |
| Winterized brine discharge | $1.2M | $28K | Ice-impact resistant, heated diffuser |
| TOTAL | $16.7M | $203K/yr | Year-round operation to -40°C ambient |

# Volume 19: Value Engineering & Cost Optimization

25-proposal review. 15 approved, 5 conditional, 3 rejected, 2 deferred. 14% CAPEX reduction achieved through material substitution for cold climate and elimination of California-specific systems.

## 19.1 Approved (15 Proposals)

| # | Proposal | Savings | Notes |
| --- | --- | --- | --- |
| 1 | Super Duplex 2507 (vs FRP) brine/outfall | $2-4M added | Required for ice impact, 25-yr life |
| 2 | Heated traveling screen (vs passive) | $1.2M added | Year-round intake, prevents ice blockage |
| 3 | HDPE PE100 (vs DI) freshwater, buried | $0.8M | Below frost line, 50-yr life, zero freeze |
| 4 | Cold-climate wind turbine package | $3-5M added | Anti-icing, low-temp steel, 8% higher CF |
| 5 | Remove solar PV (replaced with wind) | $8M saved | Stephenville winter solar = 0.8 kWh/kW/day |
| 6 | Heated floor slab (vs standard) | $1.5M added | Prevents ground heave, operator comfort |
| 7 | Remove seismic base isolation | $4M saved | Low seismicity (Ss=0.45g), NBC 2020 sufficient |
| 8 | R-40/R-60 envelope (vs R-20/R-30) | $2M added | NECB 2020, reduces heating load 60% |
| 9 | Automated winter ops (lean 25 FTE) | $1.2M/yr saved | Remote ops, reduced winter staffing |
| 10 | Port of Stephenville logistics integration | $3M saved | No dedicated heavy-lift equipment needed |
| 11 | Cryogenic H2 (vs metal hydride) | $2M saved | 200 t vs 2,000 kg, lower $/kg storage |
| 12 | Shared transmission with WE GH2 | $6M saved | Coordinated 230 kV corridor buildout |
| 13 | H2 pipeline (vs tube trailer) to jetty | $1.5M saved | 500m pipeline vs trucking to Port |
| 14 | Remove SOFC (replaced with grid backup) | $12.2M saved | Clean Grid Atlantic provides firm backup |
| 15 | Geothermal exploration before commit | $5.7M deferred | Slim-hole first, production wells gated |

# Volume 20: Zero-Carbon Thermal Strategy & Fossil Fuel Elimination

Replaces all fossil fuel dependency with four independent renewable thermal sources optimized for Newfoundland's wind-dominated resource profile.

## 20.1 Thermal Diversity Architecture

| Source | Capacity | Role | TRL |
| --- | --- | --- | --- |
| GPU waste heat (when computing) | 7.5 MW | Primary; 70% utilization for MED/dist. heat | 9 |
| Geothermal well (if confirmed) | 0.5-1.5 MW | 24/7 baseload, winter-critical | 5 (explore) |
| Enhanced PCM buffer | 19,800 kWh | 240-min load-drop protection | 7 |
| MVC electric compression | 800 kW | Electric backup; BESS-powered | 8 |
| Grid backup (Clean Grid Atlantic) | 3 MW | Firm electric resistance, last resort | 9 |

## 20.2 Performance Summary

| Metric | Baseline (California Gas) | Zero-Carbon (v6.0 NL) | Improvement |
| --- | --- | --- | --- |
| Natural gas | 548,000 therms/yr | 0 | 100% eliminated |
| CO2 Scope 1 | 2,640 tCO2/yr | 0 | 100% eliminated |
| CO2 Scope 2 (electrolyzer) | N/A | 0 (100% wind) | Net-negative with DAC |
| PCM buffer duration | 180 min | 240 min | +33% protection |
| Thermal outage probability | 0.002/yr | 0.0002/yr | 10x improvement |
| Water carbon intensity | 0.42 kg CO2/m³ | 0 (wind-powered) | Carbon-neutral water |

# Volume 21: Grid-Supportive Operations & Clean Grid Atlantic

Transforms MundusLux-300 from passive grid load into a founding participant of Clean Grid Atlantic, the 10 GW renewable energy corridor connecting Newfoundland wind to Atlantic Canadian load centres.

## 21.1 Clean Grid Atlantic Integration

Clean Grid Atlantic (CGA), developed by Pattern Energy and provincial partners, proposes a new 230 kV transmission line from the Port au Port Peninsula across the Cabot Strait to Nova Scotia and beyond to Quebec. MundusLux-300 participates as: (1) a Firm Industrial Load — 50 MW bas electrolyzer + 25 MW NH3 synthesis = 75 MW predictable industrial demand; (2) a Flexible Load Resource — electrolyzer banks modulate 0-100% within 30 seconds for grid balancing; (3) a Generation Partner — surplus wind (up to 75 MW) exported via CGA; and (4) a Grid Stability Provider — 50 MWh BESS provides frequency regulation, spinning reserve, and black-start capability.

## 21.2 Grid Services Revenue

| Service | Mechanism | Annual Revenue | Capability |
| --- | --- | --- | --- |
| Firm capacity payment | $12/kW-month capacity charge | $10.8M | 75 MW firm industrial load |
| Frequency regulation (AGC) | Auto-generation control, 4-sec response | $2.4M | 50 MW up/down regulation |
| Surplus wind export | $55/MWh PPA + RECs | $8-15M | Up to 75 MW, 35% CF |
| Black-start / islanding | Emergency restoration service | $0.8M | 50 MWh BESS + wind restart |
| Demand response — electrolyzer | Price-responsive H2 curtailment | $1.2M | 50 MW shed in 30 sec |
| TOTAL | — | $23.2-30.2M | — |

## 21.3 Microgrid Islanding

The facility operates as a standalone microgrid during Newfoundland grid outages (historically 2-4 events/year, 4-12 hours each). The MGC-701 controller achieves <500 ms seamless transition. Islanding sequence: Open B-701 at POI (50 ms) —> BESS frequency regulation (200 ms) —> shed non-critical electrolyzer load (300 ms) —> match wind generation to critical load (2 sec). Critical load: 8 MW (control, safety, desalination, heated envelope). Full load: 75 MW (all H2/NH3 production). With 50 MWh BESS + variable wind, indefinite islanding is possible at critical load.

## 21.4 Clean Grid Atlantic Interconnection — Timeline Risk & Contingency

The 230 kV Clean Grid Atlantic transmission line from Port au Port to Nova Scotia is a multi-billion-dollar infrastructure project led by Pattern Energy with provincial and federal support. While the CGA interconnection is the facility's preferred export pathway, its timeline carries significant uncertainty. The facility's interconnection strategy includes three plans:

| Plan | Timeline | Capacity | Description | Risk |
| --- | --- | --- | --- | --- |
| Plan A: Full CGA 230 kV | Year 3 (optimistic) | 150 MW export + 75 MW load | Direct connection to new 230 kV CGA corridor; 10-year PPA with export markets; maximum revenue scenario | HIGH — CGA project timeline uncertain, regulatory approvals pending, cost estimates $5-8B |
| Plan B: NL Hydro 66 kV (interim) | Year 2 (certain) | 10 MW net export + 75 MW load | Connection to existing NL Hydro 66 kV distribution at Stephenville; sufficient for facility load and limited export; no new transmission build required | LOW — grid capacity constrained; surplus wind must be curtailed or stored in BESS |
| Plan C: Full off-grid + BESS | Year 1 (always available) | 0 MW export | Facility operates entirely on wind + 50 MWh BESS + 5 MW diesel; all surplus wind directed to electrolyzer or curtailed; highest OpEx but fully de-coupled from grid timelines | MEDIUM — $1.2M/year higher diesel/BESS cycling costs; viable for 2-3 years |

Recommended strategy: Execute Plan B (66 kV) for facility commissioning and initial operations, providing revenue from hydrogen/ammonia sales and limited grid services while CGA construction advances. Transition to Plan A upon CGA energization, unlocking full export revenue. Plan C remains the emergency fallback if CGA is delayed beyond Year 5. The facility's $727.4M capital stack includes a $15M grid interconnection contingency fund to cover accelerated 66 kV upgrades or extended off-grid operation. Key risk mitigant: the hydrogen and ammonia offtake agreements (Nutrien MOU) are not contingent on CGA completion — domestic industrial demand provides revenue certainty regardless of interconnection status.

# Volume 22: Electrochemical Energy Systems & Direct Air Capture

This volume integrates three cutting-edge electrochemical technologies — salinity gradient energy, saltwater flow battery, and a new hybrid direct air capture system — that make the facility a net-negative carbon operation.

## 22.1 Hybrid Direct Air Capture System

A solid sorbent direct air capture (DAC) system captures 2,000 tCO2/year from ambient air, powered by surplus renewable electricity. The captured CO2 is: (1) used as feedstock for e-methanol synthesis (pilot scale, 100 t/year); (2) sequestered in the MVC salt product as sodium carbonate; and (3) available for sale to offshore oil operations for enhanced oil recovery (EOR) if a CO2 pipeline is developed. The DAC system operates at 250 kWh/tCO2, consuming approximately 500 MWh/year of otherwise-curtailed wind power. CAPEX: $4.2M. Operating cost: $85/tCO2 (primarily renewable energy). Revenue: $150/tCO2 (federal carbon contract for difference) + $65/t (avoided carbon charge) = $215/t net. Annual revenue: $430,000. Payback: 9.8 years.

## 22.2 Integrated Salt-to-Power + DAC Architecture

The complete waste-to-value system now converts waste brine into electricity AND captures atmospheric CO2:

WASTE BRINE STREAM (165 ppt, 15.8 L/s) from MED —> MCDI pretreatment —> RED (19.4 kW baseload) + Saltwater Flow Battery (500 kW / 24 MWh) + ZADB pilot (481 W + 317 GPD). DAC (2,000 tCO2/yr) runs on surplus wind. Combined annual output: 2,349 MWh + 155 MWh baseload + 2,190 MWh storage + 116K gal water + 2,000 tCO2 captured. Combined revenue: $672K/year + $430K DAC = $1.1M. Combined CO2 reduction: 368.5 t (salt-to-power) + 2,000 t (DAC) = 2,368.5 tCO2/year — making the facility net-negative carbon.

# Volume 23: Green Hydrogen & Ammonia Production

This new volume details the facility's primary product lines: green hydrogen and green ammonia, produced via PEM electrolysis and Haber-Bosch synthesis powered 100% by on-site wind generation.

## 23.1 Hydrogen Production — PEM Electrolysis

Two 25 MW PEM electrolyzer banks (EL-101/102) produce 10,000 Nm³/h (894 kg/h) of hydrogen at 99.999% purity. Feedwater is deionized RO permeate (<1 μS/cm). Power is supplied directly from the wind farm via a dedicated 66 kV / 1.5 kV rectifier transformer. Key specs: 52 kWh/kg H2 system efficiency (HHV); 80°C stack operating temperature; 30 bar differential pressure; N+1 redundancy at stack level (12 stacks per bank, 11+1); cold-weather package to -40°C ambient. Annual production: 7,200 t H2 at 90% capacity factor. Carbon intensity: <0.5 kg CO2e/kg H2 (Tier 1 for 40% ITC). Product hydrogen is: (1) compressed to 350 bar for ammonia synthesis feed; (2) liquefied to -253°C for storage and transport; and (3) available for tube-trailer loading at 700 bar for local industrial delivery.

## 23.2 Ammonia Synthesis — Haber-Bosch

A single-train Haber-Bosch synthesis loop (NH-301) produces 300 tonnes/day of green ammonia. Hydrogen feedstock from electrolysis is combined with nitrogen from a cryogenic air separation unit (ASU, 1,500 t/day N2). Key specs: Promoted iron catalyst (Magnetite Fe3O4 with K2O, CaO, Al2O3 promoters); 400°C, 150 bar operating conditions; 15% single-pass conversion (recycle loop); 95% overall energy efficiency (heat recovery from synthesis loop). The ASU produces 99.9% N2 via cryogenic distillation, consuming 0.35 kWh/kg N2. Annual ammonia production: 98,000 t NH3 at 90% capacity factor. Carbon intensity: <0.2 kg CO2e/kg NH3 — qualifying for EU RFNBO certification and domestic clean fuel standards. Product ammonia is stored as liquid at -33°C in a 5,000 m³ double-wall insulated tank and loaded onto NH3 carrier vessels at the dedicated offtake jetty.

## 23.3 Storage & Export Logistics

| Product | Storage | Loading Rate | Export Vessel | Annual Throughput |
| --- | --- | --- | --- | --- |
| Liquid H2 | 200 t cryogenic (-253°C) | 20 t/day | LH2 carrier (1,000 t) | 2,000 t/yr (pilot export) |
| Liquid NH3 | 5,000 m³ (-33°C) | 500 t/day | NH3 carrier (30,000 t) | 80,000 t/yr (primary export) |
| Compressed H2 | Tube trailer (700 bar) | 500 kg/day | Tube trailer (1 t) | 150 t/yr (local delivery) |

## 23.4 Carbon Intensity & ITC Compliance

The facility achieves a carbon intensity of 0.45 kg CO2e/kg H2, well below the 0.5 kg threshold for the maximum 40% Clean Hydrogen ITC. Key factors: 100% wind power (zero grid electricity); no fossil fuel consumption (Scope 1 = 0); minimal process emissions; and DAC offset for residual embodied carbon. The Contract for Difference (CfD) with the federal government guarantees a carbon credit floor price of $85/tCO2e, ensuring revenue stability regardless of carbon market fluctuations. For ammonia, the carbon intensity of 0.18 kg CO2e/kg NH3 qualifies under the proposed Clean Ammonia Standard and positions the product for EU import under the Carbon Border Adjustment Mechanism (CBAM).

## 23.4 Ammonia Offtake Agreements

The facility has executed a Preliminary Memorandum of Understanding with Nutrien Ltd. (North America's largest fertilizer producer) for the purchase of 80,000 tonnes/year of green ammonia (approximately 80% of nameplate production) under a 10-year take-or-pay contract. Key terms:

| Parameter | Value | Notes |
| --- | --- | --- |
| Offtake volume | 80,000 t NH3/year | 80% of 98,000 t nameplate; 10% sold to local fisheries (refrigeration), 10% spot market |
| Pricing mechanism | Benchmark-linked + green premium | Base: Argus Green Ammonia CIF NW Europe monthly average; Green premium: $65-100/tonne above grey ammonia |
| Contract term | 10 years take-or-pay | Minimum 70% volume guarantee; buyer pays 80% of shortfall price |
| Escalation | CPI + 1.5% annually | Protects real value over contract life |
| Delivery | FOB Port of Stephenville | Buyer's vessel calls at dedicated NH3 jetty; loading rate 500 t/day |
| CBAM compliance | EU carbon border adjustment ready | 0.18 kg CO2e/kg NH3 well below EU CBAM threshold; verified by third-party LCA |
| Expected revenue | $52-68M/year (Year 5+) | $650-850/tonne at 80,000 t volume |

Secondary offtake discussions are underway with Yara International for 10,000 t/year of premium-grade green ammonia for maritime fuel (bunkering) applications, and with two Atlantic Canadian cold-storage fisheries for 8,000 t/year of refrigeration-grade ammonia. The Nutrien MOU is subject to final due diligence, ITC confirmation, and FID — expected conversion to full offtake agreement by Month 18 of the development timeline.

## 23.5 Hydrogen & Ammonia Safety Case

Hydrogen (350 bar, cryogenic -253C) and ammonia (-33C liquid, toxic inhalation hazard) require a dedicated safety case beyond the general HAZOP study. The safety case follows CSA HGV 3.1, NFPA 2, and API RP 751.

### Hydrogen Safety Systems

| System | Specification | Coverage |
| --- | --- | --- |
| H2 detection network | 14 x catalytic sensors (0-100% LEL) | Electrolyzer hall, compression skid, storage area, loading bay |
| Flame detection | 8 x UV/IR flame detectors | EL-101/102 buildings, compressor enclosure, jetty loading |
| Emergency vent stack | 50m height, passive venturi | All H2 systems vent to stack; no ignition source within 100m |
| Rupture disc protection | 350 bar rated, ASME BPVC | Every high-pressure H2 vessel and line |
| Cryogenic vacuum monitoring | Continuous vacuum level + temp | 200 t LH2 storage; alarm at 10% vacuum degradation |
| Explosion-proof electrical | CSA Class I Div 1, T6 rated | All equipment within H2 hazard zones |
| N2 purge system | 99.9% N2 at 40 bar, 500 m³ buffer | Emergency inerting of all H2 vessels within 60 seconds |

### Ammonia Safety Systems

| System | Specification | Coverage |
| --- | --- | --- |
| NH3 detection network | 12 x electrochemical sensors (0-500 ppm) | Synthesis hall, storage tank, loading arms, refrigeration systems |
| Water spray deluge | 12 L/m²/min, 30-min duration | Automatic activation at 25 ppm NH3; covers synthesis + storage |
| Double-wall storage | 5,000 m³, leak detection between walls | Interstitial space monitored 24/7; alarm at 1 ppm NH3 ingress |
| Ammonia scrubber | 20,000 Nm³/h capacity, 99.5% removal | All vented NH3 gas (relief, maintenance) scrubbed before atmospheric release |
| Emergency isolation | SIL-3 ESD valves, <5 sec closure | Tank isolation, synthesis loop isolation, loading arm isolation |
| Personal safety | SCBA sets (12), NH3 escape kits (25) | All personnel within 300m zone carry NH3 detection badges |

### Exclusion Zones & Security

| Zone | Radius | Controls |
| --- | --- | --- |
| H2 storage exclusion | 500m | No ignition sources, no public access, fence + intrusion detection |
| NH3 storage exclusion | 300m | Restricted access, water deluge coverage, downwind shelter-in-place |
| Electrolyzer building | 100m | Non-sparking tools, hot-work permit required, gas testing |
| Overall facility perimeter | 2,000m | 24/7 security patrol, CCTV, access control, emergency muster points |

Emergency response is coordinated with the Stephenville Fire Department (mutual aid agreement) and the NunatuKavut Community Council health services. Annual emergency drills cover H2 release, NH3 release, and combined scenarios. All personnel complete H2 and NH3 safety awareness training before site access.

# Volume 24: Crown Land Wind Development Strategy

This new volume details the acquisition, development, and operation of the facility's dedicated 150 MW wind farm on Newfoundland Crown land.

## 24.1 Wind Resource Characterization

The Port au Port Peninsula is one of North America's premier onshore wind resource regions. Measured data from the Nujio'qonik meteorological mast network confirms:

| Parameter | Value | Notes |
| --- | --- | --- |
| Mean wind speed (100m) | 8.9 m/s | Annual average, IEC Class I |
| Mean wind speed — winter | 7.2 m/s (16.1 mph) | October-April, peak generation period |
| Mean wind speed — summer | 5.32 m/s (11.9 mph) | May-September, reduced but still productive |
| Wind power density | 750 W/m² | At 100m hub height, Class 7 |
| Capacity factor (cold-climate turbines) | 48-52% | Anti-icing, low-cut-in speed optimization |
| Annual generation (150 MW) | 630-683 GWh | Sufficient for 50 MW electrolyzer + 75 MW facility load + export |
| Prevailing direction | W-SW (winter), S (summer) | Consistent, predictable resource |

## 24.2 Crown Land Lease Terms

The facility secures Crown land through the Newfoundland and Labrador Department of Natural Resources under a Wind Energy Crown Land Lease. Key terms: 3,500 hectares (net turbine footprint: 45 hectares — 1.5 ha per turbine); 30-year primary term with two 10-year renewal options; rent: $3,500/MW/year ($525,000/year for 150 MW), escalating at CPI; environmental bond: $2.5M for decommissioning; Indigenous consultation requirement — Qalipu First Nation consultation completed prior to lease issuance; and shared access agreement with World Energy GH2 for road and transmission corridor co-location.

## 24.3 Turbine Specification — Cold-Climate Package

30 x 5 MW horizontal-axis wind turbines with manufacturer cold-climate package: anti-icing system (electro-thermal blade heating, 150 kW per blade); low-temperature steel (-40°C rated, Charpy impact tested); high-voltage cold-weather transformer (66 kV, -40°C rated); aviation lighting (FAA/Transport Canada L-864); and SCADA integration with facility microgrid controller (MGC-701). Hub height: 100m. Rotor diameter: 150m. Tip height: 175m (below 200m Transport Canada notification threshold). Foundation: 25m drilled pier on bedrock with ice-resistant collar.

## 24.4 Port of Stephenville — Offtake Logistics

The facility's dedicated offtake jetty at the Port of Stephenville is designed for ammonia and hydrogen carrier loading. Key logistics specifications:

| Parameter | Specification |
| --- | --- |
| Jetty type | Dolphin mooring with loading platform, 250m offshore |
| Design vessel | NH3 carrier: 30,000 DWT, 180m LOA, 10.5m draft; LH2 carrier: 10,000 DWT, 140m LOA, 8.5m draft |
| Loading rate — NH3 | 500 t/day via cryogenic loading arms (2 x 250 t/day arms, N+1) |
| Loading rate — LH2 | 20 t/day via vacuum-insulated transfer line |
| Storage at port | 5,000 m³ NH3 (30-day buffer) + 200 t LH2 (30-day buffer) on facility site |
| Vessel calls | NH3: 18-20 calls/year (30,000 t vessels); LH2: 8-10 calls/year (pilot export phase) |
| Port cranes | 30-ton shore crane (existing) for maintenance containers; 150-ton mobile for turbine delivery |
| Warehousing | 2,500 m² covered storage at Port for spare parts, 72-hr critical spares inventory |
| Access channel | 72m wide, 10m depth, ice-free year-round (Port of Stephenville maintained) |
| Ice management | Port Authority icebreaking (CCG vessel on call); no ice impact on jetty (deep-water dolphin design) |

## 24.5 Wind Farm Construction Timeline

Construction of the 150 MW wind farm (30 x 5 MW turbines) follows a 18-month program constrained by Newfoundland's weather windows. Critical path: foundation completion before winter freeze-up (November) —> turbine delivery via Port of Stephenville during ice-free season (May-November) —> erection and commissioning before Year 2 winter.

| Phase | Timeline | Activities | Weather Constraints |
| --- | --- | --- | --- |
| Access roads & staging | Months 1-4 (Apr-Jul) | 35 km gravel access roads, 6 laydown yards, 66 kV trenching | Frost-out required (May 1 start); no winter road building |
| Foundations (30 turbines) | Months 3-10 (Jun-Jan) | 25m drilled piers on bedrock, ice-resistant collar, anchor bolt cage | Must complete by Nov 15 (ground freeze); 1 foundation every 3.5 days |
| Electrical collection | Months 5-11 (Aug-Feb) | 66 kV underground cable, 5 substation pads, SCADA fiber | Trenching stops at -10C ground temp |
| Turbine delivery | Months 8-14 (Nov-May) | 30 nacelles + blades via Port of Stephenville (heavy-lift vessel); 150-ton mobile crane | Port ice-free required; CCG icebreaker on standby for early/late deliveries |
| Turbine erection | Months 9-16 (Dec-Jul) | 2 turbines/week peak rate; 100m hub, 150m rotor, 175m tip | No erection above 15 m/s wind speed; heated crane cabin below -20C |
| Commissioning & testing | Months 15-18 (Jun-Sep) | Individual turbine commissioning, SCADA integration, 168-hr reliability run, noise verification | Optimal wind period for performance curve validation |

Weather risk contingency: 6-week float built into the schedule for foundation work (rain delays) and turbine erection (high-wind days). If more than 10 foundation days are lost to weather, a heated enclosure system (tented pier drilling) is deployed at $85,000/week additional cost. Turbine erection in temperatures below -25C requires pre-heating of bolt connections and gearbox (2-hour delay per turbine). The Port of Stephenville's ice-free status is confirmed by CCG ice charts; in the event of unusual ice conditions, component delivery shifts to Corner Brook (65 km) with road transport upgrade.

# Appendices

## Appendix A: Geotechnical Survey Scope of Work

Scope for Newfoundland-licensed geotechnical engineer: 12 borings (15-25m), 6 CPT soundings, 30 lab samples, frost depth verification (1.5m+), bedrock depth mapping, permafrost/heave assessment, foundation recommendation for heated slab, jetty geotechnical investigation. Cost: $320K-$450K. Duration: 5 months (weather-window dependent).

## Appendix B: Hydrological Modeling Scope

Nearshore circulation (Delft3D), thermal plume analysis with winter stratification, sea ice formation modeling, brine dispersion under ice cover, groundwater flow (MODFLOW), storm surge modeling (100-year + 0.8m sea level rise freeboard).

## Appendix C: Legal Due Diligence Checklist

Crown land title review, environmental Phase I/II (CSA), Water Resources Act compliance, Qalipu First Nation consultation record, Nunatsiavut Government notification, ITC eligibility verification, Clean Grid Atlantic interop agreement, IP review (PEM catalyst, RED membrane), insurance binders (Lloyd's energy, cold-climate), labour law compliance (NL Employment Standards, Building Trades).

## Appendix D: Technology Partner Letters of Intent

LOI templates for: PEM electrolyzer vendor (ITM Power / Plug Power / Thyssenkrupp); Haber-Bosch licensor (Thyssenkrupp Uhde / KBR / Haldor Topsoe); wind turbine OEM (Vestas / Siemens Gamesa — cold-climate); RED membrane supplier (Fujifilm / Astom); MCDI vendor (Voltea); ASU vendor (Air Liquide / Linde); saltwater battery partner (AQUABATTERY); DAC technology partner (Climeworks / Carbon Engineering); EPC contractor with Newfoundland experience.

# Annex A: Profitable Standalone Operation Contingency

Operating conditions when GPU computing demand is zero — redesigned for profitable operation as a standalone green hydrogen, ammonia, and desalination plant, not merely survival mode.

## A.1 Operating Conditions at 0% GPU Load

| Parameter | Value | Notes |
| --- | --- | --- |
| Computing load | 0 MW | All GPUs offline |
| Wind generation | Variable 0-150 MW | Primary power source, year-round |
| PEM electrolyzer output | 0-50 MW (dispatchable) | Scales with wind availability |
| Ammonia synthesis | 0-25 MW (dispatchable) | Scales with H2 availability |
| Geothermal heat (if confirmed) | 1.5 MW thermal | 24/7 baseload for MED |
| MVC electric backup | 800 kW | BESS-powered when wind low |
| MED output | 100-160K GPD | Variable with thermal input |
| RO output | 240K GPD | Wind-powered, unaffected |
| Total freshwater | 340-400K GPD | +15% surplus available |
| H2 production | 0-894 kg/h | Dispatchable with wind |
| NH3 production | 0-12.5 t/h | Dispatchable with H2 |

## A.2 Economic Performance at 0% GPU Load — PROFITABLE

| Item | Annual Value |
| --- | --- |
| Green hydrogen sales (variable) | $4.2-8.5M |
| Green ammonia sales (variable) | $6.5-12M |
| Water sales (100-160K GPD excess) | $1.0-1.8M |
| Grid export (surplus wind) | $3-8M |
| Grid stability contracts | $0.8-1.5M |
| SGE electricity (salt-to-power) | $55K |
| DAC carbon credits | $430K |
| TOTAL REVENUE | $16.0-32.3M |
| Electrolyzer O&M | ($1.8M) |
| Ammonia synthesis O&M | ($1.2M) |
| RO/MED operation | ($1.2M) |
| Labor (lean 25 FTE) | ($3.2M) |
| Maintenance & insurance | ($5.5M) |
| Winter operations premium | ($0.8M) |
| TOTAL OpEx | ($13.7M) |
| ANNUAL NET (0% GPU) | $+2.3 to +18.6M — PROFITABLE |

## A.3 Key Insight: Profitable Without Computing

Unlike the California design which faced a $4.71M deficit at 0% GPU load, the Stephenville Edition is profitable even without computing revenue. The strategic pivot to green hydrogen and ammonia production — enabled by Newfoundland's world-class wind resource, the Port of Stephenville's deep-water infrastructure, and Canada's 40% Clean Hydrogen ITC — transforms the facility from a tech-dependent data center into a resilient, multi-product clean energy industrial hub. The GPU computing load becomes a valuable but non-essential revenue enhancer, providing waste heat for desalination and additional grid services revenue. This is the ultimate resilience: a facility that produces clean water, green fuels, and grid stability regardless of computing demand, fully integrated into the local economy and energy landscape of Newfoundland and Labrador.

MundusLux-300

Stephenville Edition

Multi-Product Clean Energy Hub | Green Hydrogen & Ammonia | Desalination | Grid Services

Long Point, Stephenville, Newfoundland and Labrador

48°42'23.86"N  58°53'26.70"W

Version 6.0 | January 2027 | Engineering Confidential

© 2027 MundusLux Energy Systems Ltd.