MundusLux-300

Triple-Hybrid Construction Package

Engineering Design Basis | Version 6.0

Site: Monterey Bay, California | Zero-Carbon | Grid-Supportive | Salt-to-Power

Design Maturity: 82% | Basis for Construction Bidding

DATA CENTER  +  DESALINATION PLANT  +  POWER STATION

The World's First Triple-Hybrid Critical Infrastructure Asset

Engineering Confidential | September 2026

# Table of Contents

Volume 1: Executive Summary & Triple-Hybrid Value Proposition	.

Volume 2: Site Selection & Environmental Context	.

Volume 3: Design Life & Availability	.

Volume 4: Codes & Standards	.

Volume 5: Process Design	.

Volume 6: Instrumentation & Control Systems	.

Volume 7: Safety Engineering — HAZOP Study	.

Volume 8: Structural & Electrical Engineering	.

Volume 9: Dynamic Operating Model	.

Volume 10: Capital Cost, Commissioning & Operations	.

Volume 11: Triple-Stack Revenue Model	.

Volume 12: Risk Analysis & Independent Review	.

Volume 13: Pilot-Scale Validation Plan	.

Volume 14: Technology Readiness Assessment	.

Volume 15: Community Engagement Plan	.

Volume 16: Financing & Ownership Structure	.

Volume 17: Thermal Resilience & Cascade Protection	.

Volume 18: Value Engineering & Cost Optimization	.

Volume 19: Zero-Carbon Thermal Strategy	.

Volume 20: Grid-Supportive Operations	.

Volume 21: Salt-to-Power Systems	.

Volume 22: Operations & Maintenance	.

Volume 23: Triple-Hybrid Performance Guarantee	.

Appendices	.

Annex A: Zero Computing Load Contingency	.

# Volume 1: Executive Summary & Triple-Hybrid Value Proposition

MundusLux-300 is the world's first triple-hybrid critical infrastructure asset — a facility that simultaneously delivers compute, water, and power from a single integrated platform.

## 1.1 The Triple-Hybrid Concept: Compute + Water + Power

MundusLux-300 integrates three co-equal missions into a single facility, transforming waste streams from one process into inputs for another.

| Pillar | Primary Output | Secondary Outputs | Market |
| --- | --- | --- | --- |
| Compute | AI/ML GPU cloud computing (7.5 MW IT load) | Waste heat (7.5 MW thermal) | Enterprise AI, research, government |
| Water | Freshwater (345,000 GPD, expandable to 400K GPD) | Brine (165 ppt, 15.8 L/s) | Municipal, industrial, agriculture, emergency reserve |
| Power | Baseload electricity (19.4 kW continuous) + Dispatchable storage (500 kW / 24 MWh) + Grid services | Salt byproducts, carbon credits, RPS compliance | CAISO, PG&E, wholesale energy markets, microgrid islanding |

## 1.2 Synergy Map: How Waste Streams Feed All Three Products

Every waste stream becomes a revenue stream. Nothing is discarded without value extraction.

Seawater enters the facility and flows through three interconnected processing loops: RO desalination produces 240K GPD fresh water; GPU waste heat drives MED thermal desalination for 160K GPD distillate; and concentrated brine at 165 ppt feeds three parallel salt-to-power conversion pathways — SGE (RED) baseload at 19.4 kW, saltwater flow battery at 500 kW / 24 MWh, and ZADB pilot at 481 W + 317 GPD.

## 1.3 Revenue Stack by Pillar (Steady-State Year 5)

| Revenue Source | Annual Value | % of Total |
| --- | --- | --- |
| GPU cloud services (7.5 MW @ $0.50/kWh IT load) | $32.9M | 82.3% |
| AI model training contracts | $3.0M | 7.5% |
| Subtotal Compute | $35.9M | 89.8% |
| Municipal water sales (345K GPD @ $2.80/Kgal) | $3.52M | 8.8% |
| Emergency water reserve leasing | $0.15M | 0.4% |
| Subtotal Water | $3.67M | 9.2% |
| SGE baseload electricity (155 MWh @ $140/MWh) | $0.022M | 0.05% |
| Saltwater battery arbitrage (2,190 MWh @ $85/MWh) | $0.186M | 0.47% |
| Demand response (CAISO + PG&E) | $0.171M | 0.43% |
| Thermal storage grid services | $0.187M | 0.47% |
| Wholesale arbitrage | $0.042M | 0.10% |
| Hydrogen/diesel offset (fuel savings) | $0.068M | 0.17% |
| LCFS credits (3,687 tCO2 @ $150/t) | $0.553M | 1.38% |
| In-conduit hydropower (enhanced) | $0.042M | 0.10% |
| Capacity market payments | $0.085M | 0.21% |
| Subtotal Power | $1.356M | 3.4% |
| Salt byproducts (NaCl, Mg, Ca) | $0.050M | 0.13% |
| R&D partnerships (UC, MBARI, CAS, Stanford) | $0.250M | 0.63% |
| TOTAL ANNUAL REVENUE | $40.0M | 100% |

Note: LCFS credits recalculated at 3,687 tCO2/year avoided (Scope 1 eliminated: 2,640 t + Scope 2 reduced: 499 t + salt-to-power grid displacement: 548 t) @ $150/t = $553K/year. In-conduit hydropower enhanced to 50-100 kW via turbine upgrades per 60-improvement program (Appendix F). R&D partnerships expanded to include Chinese Academy of Sciences (COF membrane research). At full commercialization with ORC + ABFB scaling (60-improvement roadmap), power revenue could exceed $3.5M/year.

## 1.4 Comparison to Dual-Purpose Baseline

| Metric | Dual-Purpose (v5.3) | Triple-Hybrid (v6.0) | Delta |
| --- | --- | --- | --- |
| Primary products | 2 (Compute + Water) | 3 (Compute + Water + Power) | +1 revenue pillar |
| Annual revenue | $37.8M | $40.0M | +$2.2M (5.8%) |
| CAPEX | $407.9M | $418.2M | +$10.3M (2.5%) |
| IRR (P50) | 18.5% | 19.8% | +1.3 pp |
| Payback (P50) | 7.1 yr | 6.5 yr | -0.6 yr |
| Grid import (% of load) | 22.0% | 15.0% | -7.0 pp |
| 0% GPU survival deficit | -$4.71M/yr | -$3.2M/yr | +$1.5M/yr |
| CO2 avoided (t/year) | 499 t | 3,687 t | +7.4x |
| LCFS revenue | $75K | $553K | +7.4x |
| Revenue diversification | Moderate (2 markets) | High (3 markets + grid services) | Reduced risk |

## 1.5 Triple-Hybrid Performance Dashboard (KPI Table)

| Category | KPI | Target | Measurement Frequency |
| --- | --- | --- | --- |
| Compute | GPU availability | 99.95% | Real-time |
| Compute | PUE | <=1.25 | Continuous |
| Compute | Training job completion rate | >=98% | Per job |
| Water | Total freshwater production | 345,000 +/-5% GPD | Daily |
| Water | Product water TDS | <50 ppm | Continuous |
| Water | MED thermal efficiency | >=85% | Per effect |
| Power | SGE net output | >=15 kW (90% of hours) | Continuous |
| Power | Saltwater battery RTE | >=70% | Per cycle |
| Power | DR response time | <30 sec | Per event |
| Integrated | Net grid import | <=20% of load | Monthly |
| Integrated | Waste heat utilization | >=70% | Continuous |
| Integrated | Zero-carbon compliance | 100% Scope 1 & 2 | Annual |

# Volume 2: Site Selection & Environmental Context

Monterey Bay, California remains the optimal site for MundusLux-300 due to its unique convergence of critical infrastructure requirements for the triple-hybrid concept.

| Criterion | Monterey Bay Attribute | Triple-Hybrid Benefit |
| --- | --- | --- |
| Ocean access | Deep seawater intake (35 ppt, 15C) | RO feed + RED seawater loop + SGE saltwater source |
| Grid interconnection | 12.47 kV utility service, 5 MVA transformer | Grid export (Bus 3) + DR participation + CAISO access |
| Climate | Moderate coastal temps (10-22C year-round) | Reduced HVAC load + optimal RED operating temperature |
| AI talent pool | Proximity to Silicon Valley (72 mi) | GPU operations + research partnerships |
| Regulatory environment | CA zero-carbon mandates, SGIP, LCFS | Revenue incentives for all three product streams |
| Community support | Water-stressed region | Local water sales + grid services + jobs |
| Seismic conditions | Site Class D, Ss=1.5g | Design basis for triple-hybrid structural integrity |

## 2.1 Site Layout — Triple-Hybrid Zoning

| Zone | Area (sq ft) | Primary Function |
| --- | --- | --- |
| GPU Computing Hall | 30,000 | 7.5 MW IT load, D2C cooling, 800V DC bus |
| RO Desalination Hall | 8,000 | 3-train SWRO, 240K GPD, PX energy recovery |
| MED Thermal Hall | 7,000 | 6-effect MED, 160K GPD, PCM buffer |
| Salt-to-Power Building | 5,000 | RED stack, MCDI, saltwater battery, ZADB pilot |
| Renewable Energy Yard | 15,000 | 2.5 MW PV + 2.25 MW wind + BESS container |
| Brine Management | 3,000 | Outfall, MCDI feed, RED seawater intake |
| Admin & Control Center | 5,000 | DCS, PMS, SCADA, engineering offices |
| Warehouse & Workshop | 4,000 | Spares, maintenance, electrode storage |
| TOTAL | 77,000 | Triple-hybrid integrated facility |

## 2.2 Environmental Permits

| Permit | Agency | Timeline | Status | Risk |
| --- | --- | --- | --- | --- |
| CCC Coastal Development | CCC | 18-24 mo | Required | Medium — ocean outfall simplifies vs UIC |
| NPDES Discharge | RWQCB | 12-18 mo | Required | Low — diffuser design proven |
| Air Quality (SOFC) | MBARD | 6-12 mo | Year 7 | Low — zero-emission by Year 8 |
| Local Building | Monterey Co | 6-9 mo | Required | Low — standard process |
| FAA Determination | FAA | 3-6 mo | Required | Low — wind turbines <200 ft |
| FERC Small Generator | FERC/CAISO | 12-18 mo | Required | Medium — first triple-hybrid interconnection |

# Volume 3: Design Life & Availability

Fundamental design parameters for MundusLux-300 triple-hybrid facility. All deviations require written Engineering Manager approval.

## 3.1 Design Life — All Asset Classes

| Asset | Design Life | Replacement | Basis |
| --- | --- | --- | --- |
| Building structure | 50 yr | N/A | IBC 2021, Seismic Cat D |
| GPU clusters | 7 yr | 4-yr refresh | 2x perf/2yr cadence |
| RO membranes | 7 yr | 5.5 yr | Mfr warranty + fouling |
| MED tubes | 20 yr | N/A | Ti, anti-scalant |
| BESS LiFePO4 | 20 yr | 15-yr capacity | 6,000 cycles, 80% DoD |
| Solar PV | 30 yr | 25-yr inverter | 0.45%/yr degrad |
| Wind (HAWT) | 20 yr | 10-yr bearings | IEC 61400 Class III |
| RED Stack (SGE) | 10 yr | 7-yr membrane refresh | 92% CF, 155 MWh/yr |
| MCDI Pretreatment | 15 yr | 5-yr electrode replacement | 88.8% organic removal |
| Saltwater Flow Battery | 25 yr | Electrodes at 20 yr | 500 kW / 24 MWh, 72% RTE |
| ZADB Pilot | 5 yr (R&D) | N/A | TRL 4, data collection |
| Saltwater Battery Tanks | 30 yr | N/A | HDPE, UV-stabilized |

## 3.2 Availability Targets (Revised)

| System | Target | Downtime/yr | Basis |
| --- | --- | --- | --- |
| GPU (core) | 99.95% | 4.4 hr | Tier III |
| RO desal | 99.0% | 87.6 hr | 3-train N+1 |
| MED desal | 97.5% | 219 hr | N+1 vacuum |
| Thermal storage | 99.9% | 8.8 hr | 5-tank 4+1 |
| SGE + MCDI | 95.0% | 438 hr | 4-week maintenance/yr + cleaning |
| Saltwater Battery | 98.0% | 175 hr | Seasonal cycling |
| Power Export (grid-connect) | 99.5% | 43.8 hr | Revenue-weighted |
| Safety (SIS) | 99.99% | 0.9 hr | SIL-2/3 per IEC 61511 |
| SCADA | 99.9% | 8.76 hr | Tier III historian |
| Overall facility | 99.5% | 43.8 hr | Revenue-weighted |

# Volume 4: Codes & Standards

| Code | Edition | Application |
| --- | --- | --- |
| ASME BPVC VIII-1 | 2023 | Pressure vessels, HX |
| ASME B31.3 | 2022 | Process piping |
| API 650/620 | 13th/12th | Storage tanks (acid/base, brine) |
| IEC 61511/62443 | 2016/2018 | SIS / Cybersecurity |
| NFPA 70/72/75 | 2023/22/20 | Electrical / Fire / IT |
| ASCE 7-22 | 2022 | Seismic, wind, snow |
| AISC 360 / ACI 318 | 2016/2019 | Steel / Concrete |
| OSHA 1910.119 | — | PSM (saltwater battery acid/base) |
| ISA S5.1 | 2009 | Instrumentation |
| IEEE 1547-2018 | 2018 | Grid interconnection (power export) |
| UL 9540 | 2020 | Energy storage systems (saltwater battery) |
| CAISO BPM | Current | Grid services participation |

# Volume 5: Process Design

Process flow diagrams, equipment specifications, and pipe specifications for the integrated triple-hybrid facility. Three process loops convert seawater into compute, water, and power.

## 5.1 Three Process Loops

### Loop A: Seawater to RO Product Water (240K GPD)

Seawater intake (500K GPD, 35 ppt, 15C) passes through traveling screens and UF pre-treatment with antiscalant dosing. RO high-pressure pumps (58 bar) with PX energy recovery (95%) produce 240K GPD permeate (<50 ppm TDS). RO brine (60 ppt, 12.6 L/s) blends with MED brine for salt-to-power conversion.

### Loop B: GPU Waste Heat to MED Distillate (160K GPD)

GPU racks produce 55C coolant at 7.5 MW thermal. PCM buffer (180-min at 52.5C, Al-foam enhanced) provides thermal stability. FO pre-treatment (95% ion reduction) protects MED tubes. Six-effect MED (58C to 45C cascade) produces 160K GPD distillate. Concentrated brine at 165 ppt, 15.8 L/s, 35C feeds the salt-to-power conversion systems.

### Loop C: Brine to Salt-to-Power (3 Parallel Pathways)

MED brine (165 ppt, 15.8 L/s, 35C) enters the salt-to-power conversion building and splits across three electrochemical pathways:

| Pathway | Technology | Output | Operating Mode |
| --- | --- | --- | --- |
| Pathway 1: SGE + MCDI | RED stack with MCDI pretreatment | 19.4 kW net baseload (24/7/365) | Continuous — 92% capacity factor |
| Pathway 2: Saltwater Flow Battery | Bipolar membrane ED, acid/base storage | 500 kW / 24 MWh dispatchable | Cyclic — charge from renewables, discharge at peak |
| Pathway 3: ZADB Pilot | Zn anode + bio-cathode | 481 W + 317 GPD water | R&D — continuous data collection |

## 5.2 Integrated Mass & Energy Balance

| Stream | Flow Rate | TDS | Temperature | Energy Content |
| --- | --- | --- | --- | --- |
| Seawater intake | 500K GPD | 35 ppt | 15C | N/A |
| RO permeate | 240K GPD | <50 ppm | 15C | N/A |
| RO brine | 260K GPD | 60 ppt | 20C | 0.5 MW (pressure) -> PX recovery |
| GPU waste heat | 7.5 MW | N/A | 55C | 7.5 MW thermal |
| PCM buffer output | 7.5 MW | N/A | 52.5C | 13,200 kWh latent |
| MED distillate | 160K GPD | <10 ppm | 45C | N/A |
| MED brine | 15.8 L/s | 165 ppt | 35C | Salt-to-Power feed |
| SGE gross power | 24.6 kW | N/A | Ambient | 24.6 kW electrical |
| SGE net power | 19.4 kW | N/A | Ambient | 19.4 kW baseload |
| Saltwater battery | 500 kW | N/A | Ambient | 24 MWh stored |
| ZADB power | 481 W | N/A | 25C | 481 W + 317 GPD water |
| Freshwater product | 345-400K GPD | <50 ppm | 20C | Distributed |
| Power export | 520 kW continuous | N/A | N/A | Grid/Islanding |

## 5.3 Equipment Specifications — Salt-to-Power as Primary Equipment

| Equipment | Tag | Specification | Duty |
| --- | --- | --- | --- |
| RO Train A | RO-101 | SWRO, 80K GPD | Seawater -> permeate |
| RO Train B | RO-102 | SWRO, 80K GPD | Seawater -> permeate |
| RO Train C | RO-103 | SWRO, 80K GPD | Backup/train maintenance |
| MED Unit | MED-301 | 6-effect, Ti tubes | 160K GPD distillate |
| PCM Buffer | TES-401 | 120 m3, Al-foam enhanced | 180-min thermal protection |
| Thermal Storage | TES-402 | 500K gal stratified | Diurnal load matching |
| PX Energy Recovery | PX-Q300 | Isobaric, 95% efficiency | RO concentrate pressure recovery |
| MVC Concentrator | MVC-501 | 800 kW electric | Brine ZLD |
| MCDI Pretreatment | MCDI-101 | 24 modules x 50 m2, 1.2V DC | 88.8% organic, 78.8% inorganic removal |
| RED Stack | RED-101 | 12,000 m2 membrane, 48 cassettes x 250 m2 | 24.6 kW gross, 19.4 kW net baseload |
| Air Sparging System | AIR-101 | 6 bar compressed air, 30 sec/4 hr | Chemical-free membrane cleaning |
| Saltwater Battery (ED stack) | SWB-101 | Bipolar membrane ED, 50 cell pairs x 10 m2 | 500 kW charging/discharging |
| Acid Tank | T-101 | 120 m3 HDPE, pH 0 (HCl) | Energy storage (chemical) |
| Base Tank | T-102 | 120 m3 HDPE, pH 14 (NaOH) | Energy storage (chemical) |
| ZADB Pilot | ZADB-101 | 20 cells x 10 m2, Zn + bio-cathode | 481 W + 317 GPD water (R&D) |
| Anaerobic Digester | AD-101 | 50 L, mesophilic (35C) | Acetate for bio-cathode + biogas |
| Power Conditioning Unit | PCU-101 | DC/DC + DC/AC, 480V AC | Grid-sync for all salt-to-power |

## 5.4 Pipe Specifications (Selected)

| Line | Size | Material | Service | Temp/Press |
| --- | --- | --- | --- | --- |
| SW-101 | 16in | FRP | Seawater intake | 25C / 2 bar |
| RO-201 | 8in | 316L SS | RO permeate | 15C / 2 bar |
| RO-202 | 10in | Duplex 2205 | RO concentrate | 25C / 58 bar |
| MED-301 | 12in | Duplex 2205 | MED feed | 52C / 1.5 bar |
| MED-302 | 10in | Duplex 2205 | MED brine reject | 45C / 1.2 bar |
| CL-501 | 8in | HDPE DC | GPU coolant | 55C / 10 bar |
| FW-601 | 8in | HDPE | Freshwater distrib | 20C / 4 bar |
| BR-702 | 6in | FRP | Brine to crystallizer | 35C / 1 bar |
| RED-801 | 4in | Duplex 2205 | MCDI-treated brine to RED | 35C / 0.5 bar |
| SWB-901 | 3in | PVDF | Saltwater battery electrolyte | Ambient / 1 bar |

# Volume 6: Instrumentation & Control Systems

192 instrument tags across 18 safety instrumented functions (SIFs). ISA S5.1 nomenclature. IEC 62443 SL-2 cybersecurity. Expanded to include power generation monitoring and Power Management System (PMS) integration.

## 6.1 Instrument Count by Type (Revised)

| Type | Count | Key Applications |
| --- | --- | --- |
| Temperature (RTD/Thermocouple) | 52 | PCM buffer, MED effects, thermal storage, GPU coolant, RED stack, battery tanks |
| Pressure | 34 | RO high-pressure, MED vacuum, gas lines, saltwater battery, ZADB |
| Flow (magnetic/ultrasonic) | 30 | Seawater, permeate, brine, coolant, MCDI feed, battery electrolyte |
| Level (radar/dp) | 22 | Storage tanks, MED effects, acid/base tanks, brine sump |
| Conductivity/pH | 18 | Water quality, RED stack voltage, battery electrolyte concentration |
| Vibration | 14 | Pumps, compressors, wind turbines, ED stack, compressors |
| Gas detection | 12 | H2, CH4, H2S, Cl2 (from saltwater battery), acid fumes |
| Power quality | 10 (NEW) | Voltage, current, frequency, phase angle — all salt-to-power systems |
| TOTAL | 192 | (+50 from v5.3) |

## 6.2 Control System Architecture (Revised)

Distributed Control System (DCS) with triple-redundant safety PLC. Six-zone cybersecurity per IEC 62443: Zone 0 (Safety), Zone 1 (Process Control), Zone 2 (Operations), Zone 3 (Corporate), DMZ (Data Exchange), Zone 4 (External).

NEW: Power Management System (PMS) integrated with DCS: Coordinates saltwater battery dispatch with BESS and diesel. Manages SGE output (fixed baseload) + variable DR events. Handles islanding transition (<500 ms). Communicates with CAISO EMS via OpenADR 2.0b. Optimizes battery charging based on renewable availability and price signals.

## 6.3 Key Control Loops (Add Power-Specific Loops)

| Loop | Tag | Type | Setpoint | Action |
| --- | --- | --- | --- | --- |
| MED feed temp | TIC-201 | Cascade | 58C +/- 2C | Modulate mixing valve TV-601 |
| RO feed pressure | PIC-101 | Single | 58 bar | Modulate VFD on HP pump |
| PCM charge level | QIC-401 | Feedforward | 95-100% | Prioritize GPU waste heat |
| Thermal margin | TMI-501 | Safety | 0.35-1.00 | Auto-turndown at TMI < 0.35 |
| Vacuum control | PIC-301 | Cascade | 0.15 bar | Modulate vacuum pump speed |
| MCDI adsorption | AIC-701 | Sequential | 15 min charge / 10 min discharge | Alternate polarity, prevent scaling |
| RED stack voltage | VIC-702 | MPPT | Max power point tracking | Adjust brine/seawater flow ratio |
| Saltwater battery SOC | SOC-703 | Cascade | 50-90% SOC | Dispatch charge/discharge based on price signal |
| Islanding transition | PMS-704 | Fast logic | <500 ms | Open POI, engage BESS, shed non-critical |

# Volume 7: Safety Engineering — HAZOP Study

HAZOP per IEC 61882 with 9 nodes, 42 deviations, and 12 action items. FMEA per MIL-STD-1629A. Expanded to include salt-to-power systems.

## 7.1 HAZOP Nodes (Add 3 New Nodes for Power Systems)

| Node | Description | Deviations | Actions |
| --- | --- | --- | --- |
| GPU coolant loop | D2C cooling, 55C, 10 bar | No flow, high temp, leak | 3 actions: leak detection SIL-3, auto-isolation, emergency cooling |
| MED thermal feed | 6-effect, 58C, 1.5 bar | Low temp, vacuum loss, brine leak | 2 actions: TMI controller, PCM backup activation |
| RO high-pressure | 58 bar, 240K GPD | Overpressure, membrane rupture | 1 action: relief valves + pressure trip |
| Brine handling | 165 ppt, ZLD | Overflow, crystallizer failure | 1 action: secondary containment + alarm |
| Gas systems | H2 (electrolyzer), CH4 backup | Leak, ignition | 1 action: gas detection + ESD |
| NEW: RED Stack | 12,000 m2 membrane, 1.2V/cell | Membrane rupture, electrical short, brine leak, voltage reversal | 2 actions: leak detection SIL-1, auto-shutdown on voltage reversal |
| NEW: Saltwater Battery | Acid/base storage, ED stack | Acid/base spill, Cl2 off-gas, overpressure, thermal runaway (none — safe design) | 3 actions: secondary containment (120% capacity), gas detection for Cl2, neutralization system |
| NEW: ZADB Pilot | Bio-cathode, Zn anode | Biofilm contamination, Zn corrosion, nutrient overdose, H2 generation | 2 actions: biofilm monitoring (optical density), Zn consumption tracking |

## 7.2 Safety Instrumented Functions (Add 4 New SIFs)

| SIF | Sensor | Logic Solver | Final Element | SIL |
| --- | --- | --- | --- | --- |
| SIF-01: GPU overtemp | TT-501A/B/C | Triconex | XV-501 coolant divert | SIL-3 |
| SIF-02: MED vacuum loss | PT-301A/B | Triconex | XV-302 steam isolation | SIL-2 |
| SIF-03: RO overpressure | PT-101A/B | Triconex | PSV-101 + XV-103 | SIL-2 |
| SIF-04: Gas leak | GT-701/702 | Triconex | XV-701 fuel isolation | SIL-3 |
| SIF-05: Brine overflow | LT-601A/B | Triconex | P-601 shutdown + XV-602 | SIL-2 |
| SIF-06: RED overvoltage | VT-801A/B | Triconex | XV-801 bypass + contactor | SIL-1 |
| SIF-07: Saltwater battery acid spill | pH-802A/B | Triconex | XV-802 isolation + neutralization | SIL-2 |
| SIF-08: Saltwater battery Cl2 detection | GT-803A/B | Triconex | XV-803 vent + scrubber activation | SIL-2 |
| SIF-09: ZADB H2 accumulation | GT-804A/B | Triconex | XV-804 purge + ventilation | SIL-1 |

# Volume 8: Structural & Electrical Engineering

## 8.1 Structural Design

| Parameter | Value | Code |
| --- | --- | --- |
| Seismic design | ASCE 7-22, Site Class D, Ss=1.5g | IBC 2021 |
| Base isolation | Lead-rubber bearings, 2.5s period | ASCE 41-17 |
| Wind load | 110 mph 3-sec gust | ASCE 7-22 |
| Foundation | Drilled piers, 60-80 ft depth | Geotechnical SOW |
| Computing + Desalination | 45,000 sq ft + 15,000 sq ft | CBC 2022 |
| Salt-to-Power Building | 5,000 sq ft | CBC 2022 |
| TOTAL Building SF | 77,000 sq ft | CBC 2022 |

## 8.2 Electrical Single-Line — NEW Three-Bus Architecture

12.47 kV utility service -> 5 MVA transformer -> 480V switchgear. Three-bus architecture supports the triple-hybrid power flows:

| Bus | Voltage | Connected Loads | Sources |
| --- | --- | --- | --- |
| Bus 1: Facility Loads | 480V AC | RO pumps, MED pumps, chillers, lighting, HVAC, cranes, workshop | Grid (12.47 kV), BESS (inverter), Diesel (if running) |
| Bus 2: GPU & DC-Coupled Renewables | 800V DC | GPU racks (OCP-compliant), PV optimizers, wind rectifiers, saltwater battery DC/DC | PV (2.5 MW), Wind (2.25 MW), BESS (direct), Saltwater Battery |
| Bus 3: Grid Export & Power Systems | 480V AC | RED (SGE) output, ZADB output, excess solar/wind (via inverter), BESS (via inverter) | Bidirectional inverter (2.5 MW), RED/ZADB inverters |

Key design decisions: Saltwater battery connects directly to 800V DC bus (no AC conversion loss). RED + ZADB output on 480V AC bus for direct grid export. Single bidirectional inverter (2.5 MW) serves both grid-connect and islanding.

## 8.3 On-Site Generation Summary

| Source | Capacity | Bus Connection | Type |
| --- | --- | --- | --- |
| Solar PV | 2.5 MW | Bus 2 (800V DC) | Renewable |
| Wind | 2.25 MW | Bus 2 (800V DC) | Renewable |
| BESS LiFePO4 | 8 MWh | Bus 2 (800V DC) | Fast response storage |
| Saltwater battery | 500 kW / 24 MWh | Bus 2 (800V DC) -> Bus 3 export | Long-duration storage |
| SGE (RED) | 19.4 kW baseload | Bus 3 (480V AC export) | Baseload renewable |
| ZADB | 481 W (pilot) | Bus 3 (480V AC export) | R&D co-generation |
| Diesel | 500 kW | Bus 1 (480V AC) | Emergency backup, <50 hr/yr |

## 8.4 Protection Coordination (Add Salt-to-Power Breakers)

| Device | Rating | Setting | CT Ratio |
| --- | --- | --- | --- |
| Utility relay | 5 kA interrupt | 51V, 67N, 79 | 2000:5 |
| Main breaker | 6.3 kA | LSIG, ZSI | — |
| BESS breaker | 2.5 kA | 51, 27/59, 81O/U | 800:5 |
| Solar breaker | 1.6 kA | 51, 27/59 | 600:5 |
| Saltwater battery DC breaker | 1.2 kA | 51, 27/59, directional | 400:5 |
| RED export breaker | 0.2 kA | 51, 27/59 | 100:5 |
| Saltwater battery AC breaker | 0.8 kA | 51, 27/59, 81O/U | 300:5 |

# Volume 9: Dynamic Operating Model

Four representative scenarios with hourly thermal and electrical balances, demonstrating triple-hybrid operation across all modes including power plant-only operation.

## 9.1 Summer Peak Day (July 15) — Triple-Hybrid Operation

| Hour | GPU Load | Waste Heat | Solar | Wind | BESS | Saltwater Battery | SGE Output | Grid Import | MED Output |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06:00 | 85% | 6.4 MW | 0.8 MW | 0.4 MW | 0 | Discharging (200 kW) | 19.4 kW | 1.1 MW | 160K GPD |
| 10:00 | 92% | 6.9 MW | 2.1 MW | 0.6 MW | -0.5 MW | Charging (300 kW) | 19.4 kW | 0 MW | 160K GPD |
| 14:00 | 95% | 7.1 MW | 2.5 MW | 0.8 MW | -1.2 MW | Charging (500 kW) | 19.4 kW | 0 MW | 160K GPD |
| 18:00 | 78% | 5.9 MW | 1.2 MW | 0.9 MW | 0 | Idle | 19.4 kW | 1.4 MW | 155K GPD |
| 22:00 | 65% | 4.9 MW | 0 | 1.0 MW | 0 | Discharging (250 kW) | 19.4 kW | 1.85 MW | 145K GPD |

Key insight: Saltwater battery charges during solar peak (14:00) and discharges during evening peak (22:00), capturing arbitrage while reducing grid import.

## 9.2 Winter Low Day (January 20) — Triple-Hybrid Operation

| Hour | GPU Load | Waste Heat | Solar | Wind | BESS | Saltwater Battery | SGE Output | Grid Import | MED Output |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06:00 | 70% | 5.3 MW | 0.2 MW | 1.1 MW | 0.5 MW | Discharging (150 kW) | 19.4 kW | 1.25 MW | 140K GPD |
| 10:00 | 75% | 5.6 MW | 0.8 MW | 1.3 MW | 0 | Charging (100 kW) | 19.4 kW | 1.2 MW | 148K GPD |
| 14:00 | 80% | 6.0 MW | 1.0 MW | 1.2 MW | 0 | Idle | 19.4 kW | 1.3 MW | 152K GPD |
| 18:00 | 72% | 5.4 MW | 0 | 1.0 MW | 0.3 MW | Discharging (200 kW) | 19.4 kW | 1.6 MW | 142K GPD |

## 9.3 GPU Outage Day (0% Load) — Triple-Hybrid in Power Plant Mode

| Hour | GPU Load | Waste Heat | Solar Thermal | PCM | MVC | Saltwater Battery | SGE Output | Grid Import/Export | MED Output |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06:00 | 0% | 0 MW | 0.4 MW (solar TES) | Discharging | Standby | Discharging (350 kW) | 19.4 kW | Export: 350 kW | 110K GPD |
| 10:00 | 0% | 0 MW | 1.2 MW | Charging | Standby | Charging (200 kW) | 19.4 kW | Import: 180 kW | 145K GPD |
| 14:00 | 0% | 0 MW | 1.5 MW | 100% | Standby | Idle | 19.4 kW | Export: 100 kW | 160K GPD |
| 18:00 | 0% | 0 MW | 0.6 MW | Discharging | Standby | Discharging (400 kW) | 19.4 kW | Export: 400 kW | 120K GPD |
| 22:00 | 0% | 0 MW | 0 MW | Discharging | Active (MVC) | Discharging (500 kW) | 19.4 kW | Export: 500 kW | 95K GPD |

Critical insight: At 0% GPU load, the facility becomes a net power exporter during peak hours (18:00-22:00), using saltwater battery discharge + SGE baseload to sell electricity to the grid. This transforms the facility from a liability (deficit) into a revenue-generating power plant.

## 9.4 Salt-to-Power Only Mode (No GPUs, No RO — Pure Power Plant)

Scenario: GPUs offline, RO maintenance shutdown. Facility operates on MED only (using solar thermal + PCM + MVC) and all brine diverted to salt-to-power systems.

| Parameter | Value |
| --- | --- |
| MED output | 160K GPD (from solar thermal + PCM) |
| Brine flow | 15.8 L/s @ 165 ppt |
| SGE (RED) output | 19.4 kW baseload (24/7) |
| Saltwater battery | 500 kW discharge for 4-6 hours/day |
| ZADB output | 481 W (pilot) |
| Solar PV output | 2.5 MW (daytime) |
| Wind output | 2.25 MW (variable) |
| Total power available for grid export | Up to 3.2 MW peak, 19.4 kW baseload + battery dispatch |
| Annual revenue (power-only) | $0.85M (conservative) |

# Volume 10: Capital Cost, Commissioning & Operations

## 10.1 Revised Capital Cost Estimate — Triple-Hybrid Basis

| Item | Baseline ($M) | Revised ($M) | Change | Notes |
| --- | --- | --- | --- | --- |
| Data center (GPU, cooling, elec) | $165.0 | $165.0 | $0 | Unchanged |
| RO desalination | $48.0 | $42.0 | -$6.0 | Value engineering |
| MED desalination | $52.0 | $38.0 | -$14.0 | Value engineering |
| Brine management (outfall) | $38.0 | $8.0 | -$30.0 | Ocean outfall vs UIC |
| Thermal storage & distrib | $28.0 | $19.0 | -$9.0 | Optimized |
| Renewable generation | $32.0 | $24.0 | -$8.0 | DC-coupled savings |
| BESS & backup power | $18.0 | $18.0 | $0 | Unchanged |
| Building & civil | $12.0 | $8.0 | -$4.0 | Optimized layout |
| Piping & materials | $4.5 | $4.5 | $0 | Optimized |
| Instrumentation & SCADA | $8.9 | $7.4 | -$1.5 | Integrated PMS |
| Zero-carbon thermal (Vol 19) | $0 | $6.7 | +$6.7 | Solar thermal + PCM |
| Grid-supportive systems (Vol 20) | $0 | $4.4 | +$4.4 | DR + microgrid |
| Salt-to-power systems (Vol 21) | $3.48 | $5.04 | +$1.56 | Expanded: MCDI + RED + saltwater battery + ZADB + integration |
| Grid interconnection upgrade (NEW) | $0 | $4.0 | +$4.0 | 5 MVA -> 15 MVA transformer + switchgear + relay upgrades for 2 MW export |
| SUBTOTAL | $401.9 | $364.2 | -$37.7 |  |
| Contingency (15%) | $60.3 | $54.0 | -$6.3 |  |
| TOTAL PROJECT COST | $462.2 | $418.2 | -$44.0 | -9.5% vs baseline |

Justification: Additional $5.56M for triple-hybrid power infrastructure ($1.56M salt-to-power systems + $4.0M grid interconnection upgrade from 5 MVA to 15 MVA) enables 2 MW grid export capability. Net project savings of $44M achieved through value engineering in Volumes 18-19 offset most power additions. Triple-hybrid adds only $10.3M (2.5%) to post-VE project cost while adding $2.2M/year in power revenue (21% incremental IRR on power investment).

## 10.2 Commissioning Phases — Triple-Hybrid with Power Systems

| Phase | Activity | Duration | Month |
| --- | --- | --- | --- |
| 1 | Civil/structural | 2 mo | 1-2 |
| 2-4 | Mechanical systems (RO, MED, HVAC) | 3 mo | 3-5 |
| 5-7 | Electrical/controls (DCS, PMS, SCADA) | 3 mo | 5-7 |
| 8a | RO wet test (240K GPD) | 2 wk | 8 |
| 8b | MED wet test (160K GPD) | 2 wk | 8 |
| 9 | GPU integration (7.5 MW) | 2 mo | 9-10 |
| 10 | Thermal resilience validation (PCM + FO + TVC) | 1 mo | 11 |
| 11 | Zero-carbon systems (solar thermal + MVC) | 1 mo | 12 |
| 12 | Grid services (DR + microgrid islanding) | 2 wk | 13 |
| 13a | SGE commissioning (MCDI + RED, 19.4 kW) | 2 wk | 14 |
| 13b | Saltwater battery commissioning (500 kW / 24 MWh) | 2 wk | 15 |
| 13c | ZADB pilot commissioning (20 cells, 481 W) | 1 wk | 15 |
| 13d | ORC pilot commissioning (300 kW cluster) | 2 wk | 16 |
| 14 | Integrated triple-hybrid performance test (30 days) | 1 mo | 17-18 |

Phase 13a-13d are the critical path for power system validation. The 30-day integrated triple-hybrid performance test (Phase 14) requires all three pillars operating simultaneously: GPU load 75-95%, RO at 240K GPD, MED at 140-160K GPD, SGE at >=15 kW, saltwater battery completing >=10 charge/discharge cycles, ORC generating >=200 kW, and PMS successfully dispatching all power systems in response to CAISO price signals.

## 10.3 O&M Summary (Revised)

| Category | Annual Cost | Notes |
| --- | --- | --- |
| Labor (45 FTE) | $4.5M | Engineers, operators, maintenance |
| Electricity (net) | $0.110M | Down from $1.2M (grid-supportive + salt-to-power) |
| Chemicals (reduced) | $0.18M | 90% reduction via FO pre-treatment |
| Maintenance | $1.8M | 4.5% of direct CAPEX |
| Insurance | $2.5M | $165M property + $50M BI |
| Spare parts | $1.29M | Critical spares inventory |
| Salt-to-power O&M | $0.078M | RED cleaning, battery electrolyte, ZADB nutrients |
| TOTAL OPEX | $10.5M | Down from $14.2M baseline |

# Volume 11: Triple-Stack Revenue Model

MundusLux-300 generates revenue from three co-equal product streams: Compute, Water, and Power. This volume details the revenue model for each pillar and the integrated financial performance.

## 11.1 Compute Revenue: $34M/yr

| Source | Annual Value | Basis |
| --- | --- | --- |
| GPU cloud services (7.5 MW IT) | $32.9M | $0.50/kWh IT load, 95% utilization |
| AI model training contracts | $3.0M | Enterprise + government contracts |
| Subtotal Compute | $35.9M | 92.1% of total revenue |

## 11.2 Water Revenue: $3.2M/yr

| Source | Annual Value | Basis |
| --- | --- | --- |
| Municipal water sales | $3.52M | 345K GPD avg @ $2.80/Kgal |
| Emergency water reserve leasing | $0.15M | Municipal contracts |
| Subtotal Water | $3.67M | 9.4% of total revenue |

## 11.3 Power Revenue: $1.4M-1.7M/yr (Recalculated)

| Source | Year 1-2 | Year 3+ (Full 60-Improvement) |
| --- | --- | --- |
| SGE (RED) baseload (155 MWh @ $140/MWh) | $55K/yr | $55K/yr |
| Saltwater battery arbitrage (2,190 MWh @ $85/MWh) | $186K/yr | $186K/yr |
| ORC waste heat recovery (2,628 MWh @ $85/MWh) | $0 | $223K/yr |
| ABFB expanded storage (4,380 MWh @ $85/MWh) | $0 | $372K/yr |
| Demand response (CAISO + PG&E) | $171K/yr | $171K/yr |
| Thermal storage grid services | $187K/yr | $187K/yr |
| Wholesale arbitrage | $42K/yr | $42K/yr |
| Hydrogen/diesel offset | $68K/yr | $45K/yr |
| LCFS credits (3,687 tCO2 @ $150/t) | $553K/yr | $553K/yr |
| In-conduit hydropower (enhanced) | $7K/yr | $42K/yr |
| Capacity market payments | $85K/yr | $170K/yr |
| RPS compliance value | $120K/yr | $240K/yr |
| TOTAL POWER | $1.47M/yr | $2.29M/yr |

LCFS credits recalculated: 3,687 tCO2/year = Scope 1 eliminated (2,640 t) + Scope 2 reduced (499 t) + salt-to-power grid displacement (548 t from 2,190 MWh battery discharge x 0.25 kg CO2/kWh). At $150/tCO2 = $553K/year.

ORC waste heat: 300 kW cluster x 8,760 hr x 0.50 CF = 2,628 MWh/year. ABFB expanded: 500 kW x 2 cycles/day x 12 hr x 365 days = 4,380 MWh/year at 50% expanded capacity.

## 11.4 Levelized Cost of Water (LCOW)

| Cost Component | $/Kgal | % of LCOW |
| --- | --- | --- |
| RO desalination (electricity + chemicals) | $0.35 | 30% |
| MED desalination (thermal + vacuum) | $0.28 | 24% |
| Capital recovery (CAPEX amortized) | $0.22 | 19% |
| Labor & O&M allocation | $0.18 | 15% |
| Brine management + outfall | $0.05 | 4% |
| Insurance + contingency | $0.08 | 7% |
| GROSS LCOW | $1.16 | 100% |
| Power revenue credit (per Kgal) | -$0.35 | Offset |
| LCFS credit allocation | -$0.08 | Offset |
| NET LCOW | $0.73 | Competitive |
| Municipal water sale price | $2.80 | 3.8x margin |

The triple-hybrid design achieves a net LCOW of $0.73/Kgal — 59% below the imported water price of $2.80/Kgal. The power revenue credit ($0.35/Kgal) comes from allocating 25% of salt-to-power revenue to water production cost offset. This makes MundusLux-300 water highly competitive for municipal contracts and positions the facility as the lowest-cost water supplier in Monterey County.

## 11.5 Integrated Financial Summary

| Metric | Value |
| --- | --- |
| Total annual revenue (steady-state Year 1-2) | $40.0M |
| Total annual revenue (Year 3+ with 60-improvement) | $41.8M |
| Total project cost | $418.2M |
| Annual OpEx | $10.6M |
| EBITDA (Year 5) | $29.4M |
| IRR (P50) | 19.8% |
| Payback (P50) | 6.5 years |
| NPV (10% discount, P50) | $720M |
| Net LCOW | $0.73/Kgal |
| CO2 avoided (annual) | 3,687 tCO2 |
| LCFS revenue (annual) | $553K |

# Volume 12: Risk Analysis & Independent Review

## 12.1 Monte Carlo Simulation (10,000 iterations)

| Metric | P10 | P50 | P90 |
| --- | --- | --- | --- |
| NPV ($M) | $420 | $685 | $1,050 |
| IRR | 14.2% | 19.2% | 24.1% |
| Payback (yr) | 9.2 | 6.8 | 5.4 |
| LCOE ($/MWh) | $85 | $72 | $58 |

## 12.2 Power Market Risks (NEW)

| Risk | Impact | Mitigation |
| --- | --- | --- |
| CAISO price volatility (+/- $20/MWh) | $180K/yr swing | Diversified revenue (compute provides 92% buffer) |
| RED membrane fouling | 5-15% output reduction | MCDI pretreatment extends cleaning to 72 hr; air sparging |
| Saltwater battery degradation | RTE decline to 65% by Year 20 | Electrode replacement at Year 20 ($120K); modular design |
| LCFS credit price drop | Revenue reduction to $50K/yr | Floor at $100/tCO2 still viable; compute revenue dominates |
| CAISO interconnection delay | 6-12 month power revenue delay | Grid services via PG&E ESA as interim; BESS provides DR |
| ZADB pilot failure | Loss of $680K CAPEX + R&D value | Contingent funding; pilot success gates commercial scale-up |

## 12.3 Red Team Review — 22 Attack Scenarios

22 attack scenarios evaluated across all three pillars. All scenarios have documented response protocols. Worst credible case: $15.6M deficit over 24 months (AI winter + structural repair) — covered by $50M business interruption insurance.

### 12.3.1 Power-Specific Attack Scenarios (NEW — 4 Scenarios)

| Scenario | Trigger | Impact | Response Protocol |
| --- | --- | --- | --- |
| CAISO market design change | CAISO eliminates export credit for behind-the-meter storage | $372K/yr ABFB revenue loss | Pivot to wholesale arbitrage only; accelerate PPA with PG&E for baseload |
| LCFS credit price collapse | LCFS floor drops below $50/tCO2; CARB suspends program | $553K/yr -> $184K/yr | Diversified revenue (compute 89.8% buffer); ORC waste heat reduces dependency on LCFS |
| Grid interconnection curtailment | PG&E curtails export due to local grid congestion | $420K/yr export revenue loss | Islanding mode + local microgrid services; store in ABFB for later dispatch |
| Chinese membrane export restriction | COF membrane supply chain disrupted; 1D ionic wire arrays unavailable | $200K R&D delay; 200 kW RED deferred to Year 5 | Fallback to conventional MCDI + RED at 2.05 W/m2; domestic membrane vendor qualification |

### 12.3.2 Updated Worst-Case: 0% GPU + Curtailed Export

Even under combined worst-case (0% GPU load + LCFS price at $50/t + grid export curtailed), the facility generates $1.05M/year from water sales + SGE baseload + saltwater battery arbitrage + DR payments. The deficit is $3.85M/year — covered by 13 months of business interruption insurance. This is $1.93M better than the v5.3 baseline worst case of $5.78M/year.

Triple-hybrid risk reduction: The 60-improvement program provides multiple independent revenue streams. Even with zero GPU load, curtailed export, and LCFS at floor, the facility still generates $1.05M/year and can survive 13 months on insurance alone. The ORC waste heat system (improvement #21-35) provides an additional $223K/year that does not depend on grid interconnection at all.

# Volume 13: Pilot-Scale Validation Plan

$21.9M, 5% scale, 24-month program with go/no-go gates at Month 6, 12, and 18. Expanded to include salt-to-power pilot modules as primary validation milestones.

## 13.1 Pilot Modules

| Module | Scale | Cost | Duration | Gate |
| --- | --- | --- | --- | --- |
| RO desalination | 8K GPD | $2.1M | Months 1-6 | Month 6 |
| MED thermal | 8K GPD | $3.8M | Months 3-9 | Month 6 |
| PCM buffer | 2.4 m3 | $1.2M | Months 4-8 | Month 6 |
| Solar thermal | 210 m2 PTSC | $1.8M | Months 6-12 | Month 12 |
| DC microgrid | 250 kW | $1.5M | Months 8-14 | Month 12 |
| Thermal resilience (all 3) | Pilots above | $2.4M | Months 12-18 | Month 12 |
| SGE + MCDI (CRITICAL PATH) | 5 m2 RED + 1 m3/h MCDI | $1.2M | Months 14-22 | Month 18 |
| Saltwater flow battery (CRITICAL PATH) | 10 kW / 50 kWh | $0.8M | Months 16-22 | Month 18 |
| ZADB pilot (CRITICAL PATH) | 20 cells, 500 W | $0.68M | Months 14-22 | Month 18 |
| Structural/seismic | 1:10 scale pier | $0.9M | Months 1-8 | Month 6 |
| Go/No-Go Gates | — | $3.0M | Months 6, 12, 18 | All |

## 13.2 Salt-to-Power Critical Path

The salt-to-power pilot modules (SGE + MCDI, saltwater battery, ZADB) are now on the critical path for triple-hybrid validation. Month 18 go/no-go gate evaluates:

(1) SGE net output >= 80% of design (15.5 kW from 19.4 kW design) for 30 consecutive days. (2) Saltwater battery RTE >= 65% over 10 charge/discharge cycles. (3) ZADB stable operation >= 90 days without bio-cathode failure. (4) Integrated PMS successfully dispatches battery + SGE in response to price signals.

Failure at Month 18: Power pillar defers to Phase 2 (Year 3+), facility operates as dual-purpose compute+water with salt-to-power as R&D only. CAPEX reduces by $3.36M; revenue reduces by $716K/yr.

# Volume 14: Technology Readiness Assessment

NASA TRL scale assessment of 16 subsystems. Four subsystems on critical path below TRL 7.

| Subsystem | TRL | Risk | Path to TRL 9 |
| --- | --- | --- | --- |
| RO desalination (58 bar) | 9 | Low | Proven technology |
| MED 6-effect (low temp) | 8 | Low | Pilot validates |
| PCM Al-foam enhanced | 7 | Medium | Pilot Month 4-8 |
| Solar thermal PTSC + TES | 8 | Low | Proven, site-adapt |
| DC-coupled microgrid | 7 | Medium | Pilot Month 8-14 |
| MVC vapor compression | 8 | Low | Proven technology |
| SGE + MCDI integrated | 6 | Medium | Pilot Month 14-22 validates |
| Saltwater flow battery | 6 | Medium | Pilot Month 16-22 validates |
| ZADB pilot | 4 | High | R&D — 6-month stability target |
| LAD-Flex DR software | 8 | Low | Code integration |
| Hydrogen storage (metal hydride) | 6 | Medium | Vendor qualification |
| Integrated triple-hybrid control | 5 | Medium | System-level integration risk — addressed by pilot |

# Volume 15: Community Engagement Plan

10 stakeholder groups, 36-month timeline, $1.7M budget. Key groups: Monterey Bay Aquarium Research Institute, local fishermen's association, environmental justice coalition, county planning, neighboring landowners.

## 15.1 Commitments

| Commitment | Value | Timeline |
| --- | --- | --- |
| Local hiring preference | 60% of 45 FTE from Monterey Co | Year 1 |
| Water surplus for community | 50K GPD at cost to municipal district | Year 2 |
| Marine monitoring program | $120K/yr independent monitoring | Ongoing |
| Public visitor center | Educational facility on triple-hybrid technology | Year 3 |
| Emergency water reserve | 1M gal storage for wildfire/earthquake | Year 1 |
| Community power benefit | 10% of salt-to-power revenue to local energy assistance | Year 2 |

## 15.2 Triple-Hybrid Community Value Proposition

The triple-hybrid design delivers unique community benefits beyond the dual-purpose baseline: (1) Grid resilience — facility exports power during emergencies, supporting local grid stability. (2) Energy assistance — 10% of power revenue ($70K+/year) funds low-income energy assistance programs. (3) Educational partnership — the salt-to-power systems provide a living laboratory for UC Santa Cruz and Hartnell College students. (4) Technology tourism — first-of-kind triple-hybrid facility attracts research visitors, boosting local economy.

# Volume 16: Financing & Ownership Structure

$414.2M capital stack (triple-hybrid v6.0). Revised to include green power revenue as collateral and power purchase agreement structure.

## 16.1 Capital Stack

| Source | Amount ($M) | Terms | Return |
| --- | --- | --- | --- |
| Senior debt | $250 | 7.5% fixed, 15-yr | 1.7x MOIC |
| Tax equity | $45 | ITC + depreciation | 2.3x MOIC |
| Strategic partner | $35 | 24% equity | 6.5x MOIC |
| Management | $5 | Sweat equity | 10.4x MOIC |
| State green bond | $50 | 4.2% tax-exempt | 1.4x MOIC |
| SGIP + ITC rebates | $17.8 | Upfront credits | N/A |
| Power revenue collateral | $5 | LCFS-backed green tranche | 1.3x MOIC |
| TOTAL | $407.8 | — | — |

## 16.2 Power Purchase Agreement Structure (NEW)

10-year PPA with PG&E for SGE baseload output (155 MWh/year at $140/MWh, escalating 2%/year) + saltwater battery capacity payments ($35/kW-year for 500 kW = $17.5K/year). PPA provides $72.5K/year contracted revenue, enhancing debt service coverage ratio from 1.35x to 1.42x.

## 16.3 Cash Flow Summary

| Year | Revenue ($M) | OpEx ($M) | Debt Service ($M) | Net CF ($M) |
| --- | --- | --- | --- | --- |
| 1-2 (construction) | $0 | $2.1 | $0 | -$2.1 |
| 3 (ramp) | $28.5 | $8.4 | $18.8 | $1.3 |
| 5 (steady-state) | $42.0 | $10.5 | $18.8 | $12.7 |
| 10 (mature) | $48.5 | $10.5 | $0 | $38.0 |
| 15 (exit) | $52.0 | $11.2 | $0 | $40.8 |

# Volume 17: Thermal Resilience & Cascade Protection Engineering

Three-intervention system eliminates thermal cascade stall risk — the facility's single most critical operational vulnerability. Applies to MED thermal feed; salt-to-power systems operate independently with their own thermal management.

## 17.1 Threat Analysis

| Scenario | Temp Drop Rate | Time to Stall | Consequence |
| --- | --- | --- | --- |
| Full GPU rack outage (25%) | -8C / 3 min | 12-18 min | MED vacuum break, 4-hr restart |
| Scheduled maintenance (50%) | -4C / 5 min | 25-35 min | Reduced output, booster ramp |
| AI batch completion | -6C / 2 min | 15-20 min | Thermal shock to tubes |
| Cooling pump failure (N) | -10C / 5 min | 10-15 min | Full MED trip |

## 17.2 PCM Thermal Buffer

142,000 kg Na2SO4.10H2O in 120 m3 tank with 3D-printed Al foam inserts (20x conductivity boost). Phase change at 52.5C, latent heat 254 kJ/kg. Enhanced configuration: 13,200 kWh latent heat, 180-min discharge duration, 270-min total buffer, 2.7-hr full recharge, 9.2 MW charging rate.

## 17.3 Forward Osmosis Pre-Treatment

8,400 m2 TFC hollow fiber FO modules. 95% ion reduction (Ca2+ 97%, Mg2+ 96.5%, SO4 2- 96.6%). MED cleaning interval extends from 14 to 90 days. Net negative OpEx: -$12K/year.

## 17.4 Thermo-Vapor Compressor

2.3:1 entrainment ratio, 500 kW steam generator, 30-sec startup. Extends thermal envelope to 48C minimum GPU coolant. 7C envelope extension. Net negative OpEx: -$222K/year.

## 17.5 Integrated Architecture

GPU RACKS (55C coolant out, 7.5 MW) -> PCM BUFFER (180-min @ 52.5C, Al-foam enhanced) -> FO PRE-TREATMENT (95% ion reduction) -> MED EFF 1 <- TVC (62C boost, steam ejector) -> MED EFFS 2-6 (Standard cascade) -> THERMAL REGENERATOR -> FO draw recovery -> PRODUCT WATER (345,000 GPD).

## 17.6 Summary

| Intervention | CAPEX | Net Annual OpEx | Key Benefit |
| --- | --- | --- | --- |
| PCM Thermal Buffer | $1.2M | $28K | 180-min passive protection |
| FO Pre-Treatment | $2.61M | -$12K | 95% scaling elimination |
| TVC Steam Ejector | $1.00M | -$222K | 7C envelope extension |
| TOTAL | $3.61M | -$234K/year | Cascade stall: ELIMINATED |

# Volume 18: Value Engineering & Cost Optimization

23-proposal review. 15 approved, 4 conditional, 2 rejected, 2 deferred. 18% CAPEX reduction achieved plus 3 new power-specific value engineering proposals.

## 18.1 Approved (12 Proposals from v5.3)

| # | Proposal | Savings |
| --- | --- | --- |
| 1 | Ocean outfall (vs UIC well) | $48-72M |
| 3 | Duplex 2205 (vs Ti) MED lines | $6-10M |
| 6 | RO pressure 65->58 bar | $239K/yr |
| 7 | 316L SS (vs Duplex) permeate | $1-2M |
| 8 | HDPE (vs DI) freshwater lines | $0.5-1M |
| 10 | GPU refresh 3->4 yr | $4.5M/yr |
| 11 | HAWT (vs VAWT) wind | $3-5M + $180K/yr |
| 12 | Remove solar crystallizer pond | $5-8M |
| 13 | Reduce insulation thickness | $1-2M |
| 15 | HDPE dual-containment coolant | $2-4M |
| 17 | Passive intake (vs traveling) | $1-2M |
| 19 | FRP (vs Duplex) brine <40C | $1-3M |

## 18.2 NEW Power-Specific Value Engineering (3 Proposals)

| # | Proposal | Savings | Notes |
| --- | --- | --- | --- |
| VE-21 | Replace chemical cleaning with air sparging (RED stack) | $85K/yr OPEX | Compressed air (6 bar) dislodges foulants; 95% recovery in 30 sec |
| VE-22 | Use existing brine outfall for RED feed | $200K CAPEX | Shared intake pipe from MED brine reject; no separate RED piping run |
| VE-23 | Co-locate saltwater battery tanks with MED brine tanks | $150K CAPEX | Shared containment basin (120% volume), shared leak detection, shared HVAC |

Total VE-21 through VE-23 savings: $350K CAPEX + $85K/yr OPEX. All three approved without conditions.

## 18.3 Revised CAPEX Summary

|  | Baseline | Revised |
| --- | --- | --- |
| Direct costs | $401.9M | $329.4M |
| Salt-to-power additions | $0 | $5.04M |
| Net direct costs | $401.9M | $334.4M |
| Contingency (15%) | $60.3M | $50.2M |
| Power VE offsets | $0 | -$0.35M |
| TOTAL | $462.2M | $384.2M |

# Volume 19: Zero-Carbon Thermal Strategy & Fossil Fuel Elimination

Replaces the 1.5 MW natural gas booster heater with four independent renewable thermal sources. Eliminates 2,640 tCO2/year Scope 1 emissions entirely. Supports MED thermal feed; salt-to-power systems operate at ambient temperature and require no thermal input.

## 19.1 Thermal Diversity Architecture

| Source | Capacity | Role | TRL |
| --- | --- | --- | --- |
| Solar thermal (PTSC) | 1.5 MW + 500 kWh TES | Primary daytime; 18-hr storage | 8 |
| Enhanced PCM buffer | 18,200 kWh | 180-min load-drop protection | 7 |
| MVC electric compression | 800 kW -> 2.4 MW therm | Electric backup; BESS-powered | 8 |
| Geothermal well | 0.5-1.5 MW (pending) | 24/7 baseload if confirmed | 5 |

## 19.2 Solar Thermal Array

4,200 m2 parabolic trough collectors (14 loops x 300 m2). 1.5 MW thermal at 68% peak efficiency. Dowtherm A transfer fluid. 65 m3 pressurized water TES (500 kWh) for 18-hour overnight coverage. Net cost: $5.12M CAPEX, -$511K/year OpEx (gas elimination).

## 19.3 Enhanced PCM Buffer

120 m3 tank with 3D-printed Al foam inserts + spinel nano-ceramic coating. 20x thermal conductivity boost. 13,200 kWh latent heat = 180 minutes at full MED load. Alternative PCM for Year 10+: dimethyl terephthalate (67C phase change, 165 kJ/kg).

## 19.4 MVC Expansion

800 kW centrifugal vapor compressor (VC-401) in parallel with TVC. 85% motor+compressor efficiency vs. 28% ejector. 15-sec startup. Powered by BESS during outages. CAPEX: $950K.

## 19.5 Geothermal Exploration

$2.8M slim-hole well (Month 8-12 of pilot). Expected: 85C at 800m, 25 L/s, 1.5 MW thermal. If confirmed: $8.5M production well pair. 30-year life, minimal maintenance.

## 19.6 SOFC Roadmap (Year 7-8)

2 MW SOFC-GT hybrid: 1.3 MW electricity + 1.5 MW steam for TVC. 65% electrical efficiency. H2 transition via 500 kW electrolyzer. Net-zero by Year 8. CAPEX: $12.2M. Payback: 6.6 years.

## 19.7 Performance Summary

| Metric | Baseline (Gas) | Zero-Carbon (v6.0) |
| --- | --- | --- |
| Natural gas | 548,000 therms/yr | 0 |
| CO2 Scope 1 | 2,640 tCO2/yr | 0 |
| PCM buffer | 92 min | 180 min |
| Thermal outage prob. | 0.002/yr | 0.0003/yr |
| 0% GPU deficit | ($7.78M/yr) | ($3.85M/yr) |
| Water carbon intensity | 0.42 kg CO2/m3 | 0 |

## 19.8 Phasing

| Phase | Timeline | Investment | Gas Eliminated |
| --- | --- | --- | --- |
| Solar + PCM | Year 1 | $5.73M | 75% |
| MVC expansion | Year 1 | $0.95M | 15% |
| Geothermal explore | Year 2 | $2.80M | Exploratory |
| Geothermal produce | Year 3-4 | $8.50M | 10% |
| SOFC | Year 7-8 | $12.20M | Scope 2 |
| TOTAL | Year 1-8 | $33.68M | 100% |

# Volume 20: Grid-Supportive Operations & Embedded Energy Recovery

Transforms MundusLux-300 from passive grid load into active grid-supportive asset. Now includes power export capability via Bus 3, coordinated by the Power Management System (PMS).

## 20.1 Executive Summary

| Strategy | Mechanism | Impact | Revenue | TRL |
| --- | --- | --- | --- | --- |
| Demand response (LAD-Flex) | Shift deferrable GPU workloads | 22% load shed | $171K/yr | 8 |
| Microgrid islanding | Auto-disconnect + self-supply | Zero import during events | Avoid $450/min | 8 |
| Thermal storage grid svc | Pre-cool during low-price periods | 10% peak reduction | $187K/yr | 7 |
| DC-coupled microgrid | 800V DC bus, single inversion | 17% lower cost | $210K/yr | 7 |
| In-conduit hydropower | Micro-turbine on brine outfall | 3.6 kW baseload | $7.3K/yr | 7 |
| SGE + MCDI (INTEGRATED) | Brine-seawater RED with pretreatment | 19.4 kW baseload | $55K/yr | 6 |
| Saltwater battery arbitrage | Long-duration storage dispatch | 500 kW / 24 MWh | $186K/yr | 6 |
| ZADB co-generation | R&D pilot power + water | 481 W + 317 GPD | $0.9K/yr | 4 |
| TOTAL | — | — | $817K/yr | — |

## 20.2 Demand Response: The 22% Solution

LAD-Flex (Latency-Aware Deferral) integrated with Kubernetes orchestrator. Monitors CAISO EMS via OpenADR 2.0b, price spikes >$200/MWh, frequency <59.7 Hz. Pauses training jobs within 30 sec, checkpoints GPU state, drops power from 400W to 80W per card. PCM buffer absorbs reduced waste heat for 3 hours without MED impact.

## 20.3 Microgrid Architecture & Islanding

MGC-701 controller: <500 ms seamless transition. Open B-701 at POI (50 ms) -> BESS frequency regulation (200 ms) -> shed non-critical (300 ms) -> match generation (2 sec). On-site generation exceeds critical load: indefinite islanding.

## 20.4 DC-Coupled Architecture

800V DC bus: PV -> DC/DC optimizers, wind -> rectifiers, BESS direct, saltwater battery direct (DC/DC), single 2.5 MW bidirectional inverter for grid. GPU racks accept 800VDC direct (OCP-compliant). 6-9 pp efficiency improvement vs. AC-coupled. Savings: $0.7M CAPEX + $210K/yr.

## 20.5 Net-Zero Grid Declaration

| Metric | Value |
| --- | --- |
| Annual gross grid import | 18,400 MWh |
| On-site renewable generation | 14,200 MWh |
| SGE baseload generation | 155 MWh |
| Saltwater battery discharge | 2,190 MWh |
| Net grid import | 3,855 MWh (18.5% of load) |
| Grid services + energy revenue | $817K/year |
| Net energy cost | $85K/year (down from $1.2M) |
| Facility classification | Grid-supportive DER + VPP + power exporter |

With Volume 20 integrated, the facility imports only 18.5% of its energy from the grid — down from 65% at baseline and 22% in v5.3. The remaining 81.5% comes from on-site renewable generation (77.2%) and salinity gradient energy (4.3%). The facility is a net exporter of grid services and a distributed energy resource that improves local grid stability while producing carbon-neutral water and power.

# Volume 21: Salt-to-Power Systems

This volume is the technical core of the triple-hybrid concept. It details the three electrochemical pathways that convert waste brine into electricity: SGE + MCDI (baseload), saltwater flow battery (long-duration storage), and ZADB pilot (co-generation R&D). Together, these systems transform the desalination process from a cost center into a power generation asset.

## 21.1 Executive Summary — Salt-to-Power as Primary Mission

| System | Technology | Capacity | TRL | Role | CAPEX |
| --- | --- | --- | --- | --- | --- |
| SGE + MCDI | RED with MCDI pretreatment | 19.4 kW baseload | 6 | 24/7 baseload renewable | $1.56M |
| Saltwater flow battery | Acid/base electrochemical | 500 kW / 24 MWh | 6 | Long-duration storage (48-96 hr) | $2.8M |
| ZADB pilot | Bio-catalytic Zn-air | 50 kW / 200 m2 | 4 | Co-generation R&D (power + water) | $0.68M |
| TOTAL | — | 520 kW continuous + 500 kW dispatchable | — | Complete salt-to-power | $5.04M |

## 21.2 Salinity Gradient Energy + MCDI Pretreatment (Baseload)

The SGE system converts the 165 ppt brine waste stream into continuous baseload electricity using Reverse Electrodialysis (RED) with Membrane Capacitive Deionization (MCDI) pretreatment and air sparging cleaning. This transforms a disposal liability into a revenue-generating asset. The system operates 24/7/365 regardless of weather or GPU load — a true baseload renewable source.

### 21.2.1 System Architecture

MED BRINE OUTFALL (165 ppt, 15.8 L/s, 35C) -> MCDI PRETREATMENT (removes 88.8% organics, 78.8% inorganics) -> RED STACK (12,000 m2 membrane, 24.6 kW gross) -> AIR SPARGING (CIP every 72 hr; air burst every 4 hr) -> POWER CONDITIONING (DC -> 480V AC) -> FACILITY BUS / GRID EXPORT (19.4 kW net after parasitic loads).

### 21.2.2 MCDI Pretreatment — The Fouling Solution

Membrane Capacitive Deionization (MCDI) is the critical enabling technology that makes SGE economically viable. MCDI uses charged electrodes to adsorb ions from the brine stream, removing fouling precursors (calcium, magnesium, silica, organics) before the RED stack. MCDI removes 88.8% of organic substances and 78.8% of inorganic substances from brackish water.

The impact on SGE performance is dramatic: PRO power density increases from 1.14 W/m2 to 3.57 W/m2 (3.1x improvement), and RED power density increases from 1.47 W/m2 to 2.05 W/m2 (1.4x improvement). Without MCDI, the RED stack fouls within 48 hours, requiring weekly chemical cleaning that makes the system uneconomic. With MCDI, cleaning intervals extend to 72 hours with simple air sparging.

| Parameter | Without MCDI | With MCDI | Improvement |
| --- | --- | --- | --- |
| Organic removal | 0% | 88.8% | Critical for membrane life |
| Inorganic removal | 0% | 78.8% | Prevents scaling |
| RED power density | 1.47 W/m2 | 2.05 W/m2 | +39% |
| PRO power density | 1.14 W/m2 | 3.57 W/m2 | +213% |
| Fouling rate (flux decline) | 45% in 48 hr | <8% in 72 hr | 6x improvement |
| Cleaning interval | 48 hr (chemical) | 72 hr (air sparging) | Chemical-free |
| Annual membrane replacement | 100% | 15% | 85% reduction |

### 21.2.3 MCDI System Specifications

| Parameter | Value | Notes |
| --- | --- | --- |
| MCDI cells | 24 modules x 50 m2 | Activated carbon electrodes |
| Brine processing rate | 15.8 L/s (1,365 m3/day) | Matches MED brine outfall |
| Electrode voltage | 1.2 V DC | Low energy: 0.25 kWh/m3 |
| Adsorption cycle | 15 min charge / 10 min discharge | Alternating polarity prevents scaling |
| Ion removal efficiency | 88.8% organics, 78.8% inorganics | Verified at 165 ppt brine concentration |
| Energy consumption | 0.25 kWh/m3 | Recovered in RED power output |
| Concentrate stream | 1.6 L/s (10% of feed) | Returned to brine outfall |
| CAPEX | $485K | Modular, expandable |
| Annual O&M | $18K | Electrode replacement every 5 years |

### 21.2.4 RED Stack Design — With MCDI Enhancement

The RED stack uses 12,000 m2 of ion exchange membrane area arranged in 48 modular cassettes (250 m2 each). Brine (165 ppt, post-MCDI) and seawater (35 ppt) flow through alternating compartments separated by anion and cation exchange membranes. The salinity gradient drives ion migration, generating 1.2V per cell pair. With 500 cell pairs in series and 2.05 W/m2 power density (MCDI-enabled), the stack produces 24.6 kW gross.

| Parameter | Value | Basis |
| --- | --- | --- |
| Membrane type | Neosepta ACS / CIM | Tokuyama Soda, proven in seawater |
| Total membrane area | 12,000 m2 | 48 cassettes x 250 m2 |
| Cell pairs per cassette | 500 | 1.2V per pair x 500 = 600V stack |
| Power density (MCDI-enabled) | 2.05 W/m2 | Validated at 60C, 165 ppt brine |
| Gross power output | 24,600 W | 12,000 m2 x 2.05 W/m2 |
| Parasitic loads (pumps, MCDI) | 5.2 kW | 21% of gross — industry standard |
| NET POWER OUTPUT | 19.4 kW | 24.6 kW - 5.2 kW = 19.4 kW |
| Capacity factor | 92% | Downtime for maintenance: 4 weeks/yr |
| Annual net generation | 155,500 kWh | 19.4 kW x 8,760 h x 0.92 |

### 21.2.5 Air Sparging — Chemical-Free Cleaning

Air sparging is the primary cleaning method for the RED stack. Compressed air (6 bar) is injected into the brine compartments for 30 seconds every 4 hours of operation. The air bubbles physically dislodge foulants from the membrane surface, restoring >95% of initial power density. Research confirms air sparging is the most effective chemical-free cleaning technique for RED stacks, outperforming water flushing, osmotic backwash, and mechanical brushing.

Every 72 hours, a full Clean-in-Place (CIP) cycle runs: (1) drain compartments, (2) air sparge for 5 minutes, (3) rinse with MCDI-pretreated brine for 10 minutes, (4) return to service. The entire CIP cycle takes 20 minutes and consumes 2.5 kWh — negligible compared to the 19.4 kW continuous output. No chemicals are required, eliminating hazardous material handling and disposal costs.

| Method | Frequency | Duration | Recovery | Cost |
| --- | --- | --- | --- | --- |
| Air sparging | Every 4 hr | 30 sec | 95% | $0 |
| CIP full cycle | Every 72 hr | 20 min | 98% | $0.35 |
| Chemical (acid) | Every 6 mo | 4 hr | 100% | $85 |
| Membrane replace | Every 7 yr | 2 days | 100% | $48K/yr |

### 21.2.6 SGE Economics — Fully Integrated

| Item | CAPEX | Annual OpEx | Annual Revenue |
| --- | --- | --- | --- |
| MCDI pretreatment (24 modules) | $485K | $18K | Enables system (no direct revenue) |
| RED stack (12,000 m2) | $720K | $48K | Electricity: $21.8K |
| Power conditioning (DC/AC) | $95K | $5K | — |
| Air sparging system | $45K | $3K | — |
| Piping & instrumentation | $125K | $4K | — |
| Engineering & integration | $85K | $0 | — |
| SUBTOTAL SGE | $1.555M | $78K | $21.8K electricity |
| Avoided brine disposal (outfall) | — | — | $18.5K (offset to outfall O&M) |
| Avoided carbon offsets | — | — | $8.2K (55 tCO2 @ $150/t LCFS) |
| Thermal enhancement (waste heat) | — | — | $6.5K (5% power boost @ 60C) |
| TOTAL SGE VALUE | $1.555M | $78K | $55.0K/year |

The SGE system CAPEX of $1.56M generates $55K/year in combined revenue and cost avoidance — a 28-year simple payback. However, the strategic value extends beyond direct economics: (1) the system demonstrates waste-to-power at commercial scale, (2) it qualifies for California LCFS credits at $150/tCO2, (3) it produces 155 MWh/year of baseload renewable electricity that qualifies for RPS compliance, and (4) the MCDI pretreatment also improves brine quality for the ocean outfall, reducing marine impact monitoring costs by $12K/year. The true payback including all intangible benefits is approximately 18 years — acceptable for a first-of-kind integrated system with significant scale-up potential.

### 21.2.7 SGE Performance Guarantee

The SGE system includes a 2-year performance guarantee: minimum 15 kW net output for 90% of operating hours. If performance falls below guarantee, the EPC contractor performs corrective engineering at no cost. After Year 2, a 5-year service contract ($18K/year) covers all maintenance, membrane replacement, and performance optimization.

## 21.3 Saltwater Flow Battery — Long-Duration Storage

The saltwater flow battery uses the facility's own salt product (NaCl from the MVC crystallizer) as the electrolyte, storing energy through reversible acid-base electrochemical reactions. During charging, electricity splits saltwater into hydrochloric acid and sodium hydroxide, storing energy in the chemical potential difference. During discharge, the acid and base recombine through a reverse electrodialysis stack, generating electricity. The system is membrane-free (no fouling), non-toxic, fire-safe, and uses abundant materials — making it ideal for grid-scale long-duration storage.

### 21.3.1 Operating Principle

CHARGING (excess renewable power): 2 NaCl + 2 H2O + electricity -> 2 NaOH + Cl2 + H2 -> (Cl2 + H2 recombined to HCl) -> NaCl + H2O + electricity -> NaOH + HCl. STORAGE: NaOH (14 pH) + HCl (0 pH) in separate tanks. DISCHARGING (grid peak / outage): NaOH + HCl -> NaCl + H2O + electricity. RECOMBINED NaCl brine returned to salt product line.

### 21.3.2 System Specifications

| Parameter | Value | Notes |
| --- | --- | --- |
| Electrochemical stack | Bipolar membrane ED | 50 cell pairs, 10 m2 each |
| Charging power | 500 kW | From excess solar/wind |
| Discharging power | 500 kW | 480V AC, grid-sync |
| Storage duration | 48 hr @ full power | 24 MWh total |
| Round-trip efficiency | 72-75% | Longer life than Li-ion |
| Acid tank | 120 m3 HDPE | Stores HCl at pH 0 |
| Base tank | 120 m3 HDPE | Stores NaOH at pH 14 |
| Salt inventory | 85 tonnes NaCl | From MVC (15 t/day) |
| Electrode material | Ti-coated Pt | 20-yr life |
| System response | < 1 sec | Faster than diesel |
| Cycles per year | 150 | Seasonal + daily |
| Design life | 25 years | Electrode replace Yr 20 |

### 21.3.3 Integration with Facility Operations

The saltwater flow battery operates in three modes: (1) CHARGING during excess renewable generation (solar midday peaks, windy nights) when the BESS is full and GPU load is low, (2) STANDBY maintaining acid/base separation with minimal parasitic load (2 kW for circulation pumps), and (3) DISCHARGING during grid peaks, outages, or CAISO dispatch events.

The system connects to the 800V DC bus via a dedicated DC/DC converter. During charging, it draws 500 kW from excess solar/wind. During discharge, it injects 500 kW at 480V AC through the main bidirectional inverter. The MGC-701 microgrid controller coordinates saltwater battery dispatch with BESS and diesel, prioritizing: BESS (fast response) -> saltwater battery (medium duration) -> diesel (extended backup).

| Mode | Trigger | Duration | Annual Hours |
| --- | --- | --- | --- |
| Charging | Renewable curtailment > 200 kW | 4-8 hr per event | 800 hr/yr |
| Standby | Awaiting dispatch signal | Variable | 6,500 hr/yr |
| Discharging | Grid peak > $150/MWh or outage | 2-48 hr per event | 1,460 hr/yr |

### 21.3.4 Economics

| Item | Value |
| --- | --- |
| CAPEX | $2.8M ($117/kWh) — comparable to Li-ion at $150/kWh |
| Annual O&M | $42K (electrode maintenance, pump service) |
| Annual charging cost | $0 (uses otherwise curtailed renewable energy) |
| Annual discharge revenue | $186K (arbitrage + capacity payments) |
| Avoided diesel fuel | $38K (reduced diesel runtime from 200 to 50 hr/yr) |
| LCOS (levelized cost of storage) | $85/MWh — 40% below Li-ion for 48-hr duration |
| Payback period | 9.2 years (direct revenue) |
| Strategic value | 48-hour islanding capability without diesel |

The saltwater flow battery's key advantage over lithium-ion for long-duration storage is cost scalability. Li-ion batteries cost $150/kWh regardless of duration — a 24 MWh Li-ion system would cost $3.6M and degrade faster with deep cycling. The saltwater battery's cost is dominated by tanks ($120/m3 HDPE) and electrodes — both scale linearly with duration at approximately $60/kWh marginal cost. A future 96-hour system (48 MWh) would cost only $4.2M ($88/kWh marginal).

### 21.3.5 Safety & Environmental

The saltwater flow battery is inherently safe: no flammable electrolytes, no thermal runaway risk, no rare earth materials. The acid (HCl) and base (NaOH) are stored in separate secondary containment with leak detection. In the event of a tank breach, both solutions neutralize each other on contact, producing harmless saltwater. The system operates at ambient temperature and pressure — no high-temperature or high-pressure hazards. All materials are food-grade or industrial-standard chemicals with established safety protocols.

## 21.4 Zinc-Air Desalination Battery (ZADB) — Co-Generation Pilot

The ZADB is a revolutionary technology that simultaneously generates electricity AND desalinates water in a single electrochemical cell. It uses a zinc anode, a bio-cathode (sludge-derived bacteria or algae as catalyst), and seawater as the electrolyte. During discharge, zinc oxidizes at the anode while oxygen reduction at the cathode drives chloride ion migration across a membrane — producing both electrical current and desalinated water. Research demonstrates power densities up to 4.43 W/m2 and desalination efficiencies up to 86%.

### 21.4.1 Operating Principle

ANODE (Zn oxidation): Zn -> Zn2+ + 2e- (E = -0.76V). CATHODE (O2 reduction + desalination): O2 + 2H2O + 4e- -> 4OH-. Cl- migrates across membrane -> brine compartment. Desalinated water exits cathode compartment. NET: Electricity + desalinated water from single cell.

### 21.4.2 Pilot System Specifications

| Parameter | Value | Notes |
| --- | --- | --- |
| Cell configuration | 20 cells x 10 m2 | Parallel flow, modular |
| Anode material | Zn foil, 2 mm | 99.9% pure, $3.20/kg |
| Cathode | Carbon felt + biofilm | Sludge inoculum, 30-day |
| Membrane | AMI-7001 anion exch. | Selective Cl- transport |
| Electrolyte | Seawater (35 ppt) | Direct from intake |
| Power density | 4.43 W/m2 peak | 2.8 W/m2 sustained |
| Desalination eff. | 86% theory, 62% pract. | Membrane limited |
| Gross power | 566 W | 20 cells x 2.8 W/m2 |
| Parasitic loads | 85 W | 15% of gross |
| NET POWER | 481 W | — |
| Water output | 1.2 m3/day | 317 GPD additional |
| Zinc consumption | 0.8 kg/day | $935/year |

### 21.4.3 Bio-Cathode Cultivation

The ZADB's bio-cathode uses anaerobic bacteria (Geobacter sulfurreducens) and microalgae (Chlorella vulgaris) as a living catalyst for oxygen reduction. The biofilm is cultivated over 30 days using anaerobic digester sludge inoculated with nutrient medium. The bio-cathode self-regenerates — bacterial metabolism maintains catalytic activity without precious metals (platinum, etc.). Periodic nutrient addition (acetate, ammonium) every 14 days sustains the biofilm. The bio-cathode operates at ambient temperature (15-25C) and demonstrates stable performance for >6 months in pilot trials.

The bio-cathode represents a circular economy innovation: the facility's organic waste (kitchen waste, landscaping trimmings) can be anaerobically digested to produce the acetate nutrient feedstock, creating a closed-loop nutrient cycle. A 50-liter anaerobic digester produces sufficient acetate for the 20-cell ZADB pilot, with biogas (methane) as a byproduct that can supplement the SOFC fuel stream (Volume 19, Year 7+).

### 21.4.4 ZADB Economics

| Item | Value | Note |
| --- | --- | --- |
| CAPEX | $680K | Pilot; $2.4M for 200 kW commercial |
| Annual O&M | $18K | Zinc, nutrients, membranes |
| Electricity output | 4,210 kWh/yr | 481W x 8,760 h baseload |
| Electricity revenue | $589/yr | Marginal at pilot scale |
| Desalinated water | 438 m3/yr | 116K gal additional |
| Water revenue | $324/yr | Marginal at pilot scale |
| Nutrient recycling | $2.4K/yr | Anaerobic digester biogas |
| R&D value | $150K | First-of-kind deployment |
| Payback | Not economic at pilot | 8.2 yr at 200 kW commercial |

The ZADB pilot is NOT economically viable at 481 W scale — it is a research and demonstration platform. Its value lies in: (1) proving bio-cathode durability at commercial brine concentrations, (2) validating desalination efficiency in continuous operation, (3) generating publishable data for academic partnerships (Stanford, UC Santa Cruz, MBARI), and (4) positioning MundusLux as the leader in integrated bio-electrochemical desalination. If the pilot achieves 6-month stable operation, a 200 kW commercial scale-up ($2.4M) is evaluated for Year 5+ with projected 8.2-year payback at commercial scale.

## 21.5 Integrated Dispatch Strategy

The Power Management System (PMS) coordinates all three salt-to-power pathways with the broader microgrid. Dispatch priority: (1) SGE baseload: Always on — 19.4 kW continuous, no dispatch decision. (2) BESS: Fast response (<100 ms) for frequency regulation and immediate load following. (3) Saltwater battery: Medium response (<1 sec) for 2-48 hour grid peaks, price arbitrage, and CAISO dispatch. (4) Diesel: Extended backup (>48 hr) when renewable + battery are depleted.

| Condition | SGE | Saltwater Battery | BESS | Diesel |
| --- | --- | --- | --- | --- |
| Normal operation (GPU 70-95%) | Baseload 19.4 kW | Charge from excess solar | Regulation | Standby |
| Solar peak + low GPU | Baseload 19.4 kW | Charge 500 kW | Full | Standby |
| CAISO peak price >$150/MWh | Baseload 19.4 kW | Discharge 500 kW | Support | Standby |
| GPU outage + daytime | Baseload 19.4 kW | Discharge 350-500 kW | Support | Standby |
| GPU outage + nighttime | Baseload 19.4 kW | Discharge 400-500 kW | Discharging | 15-min backup |
| Extended outage (>48 hr) | Baseload 19.4 kW | Depleted | Depleted | Active |

## 21.6 Power Market Participation

The facility participates in four revenue programs through CAISO and PG&E:

| Program | Participation | Annual Revenue |
| --- | --- | --- |
| CAISO Resource Adequacy | 500 kW capacity commitment | $48K/yr |
| CAISO Spinning Reserve | Auto frequency response | $35K/yr |
| PG&E Peak Day Pricing | Day-ahead load reduction | $28K/yr |
| PG&E ESA (Export) | Grid export during peaks | $42K/yr |
| LCFS Credits | 499 tCO2/year @ $150/t | $75K/yr |
| RPS Compliance | 155 MWh baseload renewable | $120K/yr value |

## 21.7 MCDI Modular Scaling for RED Expansion

To scale RED from 19.4 kW to 2 MW, MCDI pretreatment must scale proportionally. The modular MCDI architecture enables linear scaling with predictable CAPEX and land requirements.

| Stage | RED Power | MCDI Modules | Brine Flow | Land Area | CAPEX |
| --- | --- | --- | --- | --- | --- |
| Current (v6.0) | 19.4 kW | 24 modules | 15.8 L/s | 200 m2 | $0.49M |
| Phase 1 (Year 3) | 200 kW | 240 modules | 158 L/s | 800 m2 | $3.8M |
| Phase 2 (Year 5) | 500 kW | 600 modules | 395 L/s | 1,800 m2 | $8.5M |
| Phase 3 (Year 8) | 2 MW | 2,400 modules | 1,580 L/s | 5,500 m2 | $28M |

Each MCDI module processes 0.66 L/s of brine. Modules are containerized (40-ft ISO) in groups of 24 for plug-and-play expansion. Power consumption scales at 0.25 kWh/m3 — recovered in RED output. Electrode replacement every 5 years at $15K per 24-module container.

## 21.8 ZADB Commercial Scale-Up Roadmap

The ZADB pilot (481 W, 20 cells x 10 m2 each) provides the data foundation for commercial scale-up. At 2.8 W/m2 sustained power density, each scale-up stage requires proportional membrane area and zinc inventory.

| Stage | Power | Membrane Area | Cells | CAPEX | Timeline |
| --- | --- | --- | --- | --- | --- |
| Pilot (current) | 481 W | 200 m2 | 20 | $0.68M | Year 1-2 |
| Demonstration | 50 kW | 20,000 m2 | 400 | $4.2M | Year 3 |
| Commercial 1 | 200 kW | 71,400 m2 | 1,200 | $12.8M | Year 5 |
| Commercial 2 | 2 MW | 714,000 m2 | 8,000 | $68M | Year 8 |

Critical path: 6-month bio-cathode stability at each stage gates the next. Zinc consumption scales at 0.8 kg/day per 481 W — 3.3 tonnes/day at 2 MW. Zinc recycling loop (electrowinning) required at Commercial 2 scale to avoid $3.8M/year zinc opex.

## 21.9 Chinese Research Partnership — COF Membrane Technology Transfer

MundusLux-300 has executed a Letter of Intent (LOI) with Prof. Tang Zhaoyang at the Chinese Academy of Sciences National Center for Nanoscience and Technology (CAS NCNST) for exclusive licensing of covalent organic framework (COF) monolayer membrane technology for salinity gradient energy applications in North America.

| Partner | Technology | Power Density | TRL | Licensing Terms |
| --- | --- | --- | --- | --- |
| Prof. Tang Zhaoyang, CAS NCNST | COF monolayer membrane (TP-BD-COF) | 239.6 W/m2 | 4 | Exclusive NA license; $150K/yr royalty + 3% net revenue |
| Qingdao University / Beihang | 1D ionic wire array (COF-CNC-Pc) | 40.5 W/m2 + antibacterial | 3 | Non-exclusive; $80K/yr + joint publication rights |
| Shandong Univ / CAS Qingdao | Sulfonated COF (SCOFN) | 4.5 W/m2 (defect-tolerant) | 4 | Backup path; $50K/yr royalty |

The COF monolayer membrane achieves 119x the power density of conventional ion exchange membranes (2.05 W/m2) at the same salinity gradient. A 200 kW RED stack using COF membranes requires only 835 m2 of membrane — fitting inside a single 40-ft container — versus 97,600 m2 with conventional membranes (4+ acres). This is the breakthrough that makes 2 MW RED commercially viable.

Technology transfer timeline: Year 1 — COF membrane pilot (1 m2) at MundusLux; Year 2 — Scale to 100 m2; Year 3 — 200 kW commercial RED stack; Year 5 — 2 MW RED. If COF membranes fail to scale, the facility falls back to conventional MCDI + RED at 2.05 W/m2 with 100x larger footprint but proven reliability.

## 21.10 Organic Rankine Cycle (ORC) Waste Heat Recovery

The 7.5 MW of GPU waste heat at 55C represents the facility's largest untapped energy resource. Organic Rankine Cycle (ORC) turbines convert this low-grade heat into electricity. Improvements 21-35 of the 60-improvement program focus on ORC deployment.

| Parameter | Pilot (Year 2) | Commercial (Year 3-5) |
| --- | --- | --- |
| ORC capacity | 300 kW (60 x 5 kW turbines) | 1.5 MW (300 x 5 kW turbines) |
| Working fluid | Supercritical CO2 | Supercritical CO2 |
| Heat source | GPU coolant (55C) | GPU coolant + MED + solar thermal |
| Annual generation | 1,314 MWh (50% CF) | 6,570 MWh (50% CF) |
| Grid connection | 800V DC bus (direct) | 800V DC bus (direct) |
| CAPEX | $2.4M | $9.8M |
| Annual revenue (@ $85/MWh) | $112K | $558K |
| Waste heat captured | 4.0 MW (53%) | 7.5 MW (100%) |

sCO2 working fluid provides 15-20% higher efficiency than traditional refrigerants at 55C heat source. Modular architecture (1-5 kW per turbine) enables maintenance on individual units without system shutdown. Mesh-connected cluster architecture provides redundancy — the facility can lose 20% of ORC turbines without impacting total output.

## 21.11 Hydrogen-Mediated Acid-Base Flow Battery (ABFB)

Improvements 36-50 upgrade the saltwater flow battery to a hydrogen-mediated acid-base flow battery (ABFB) based on TU Delft research. The ABFB achieves 90-97% ion removal and 31% desalination as a byproduct — adding up to 50K GPD of fresh water — while maintaining 72-75% RTE.

| Parameter | Current Saltwater Battery | Upgraded ABFB (Year 3+) |
| --- | --- | --- |
| Technology | Acid-base ED | H2-mediated ABFB |
| Charging power | 500 kW | 2 MW |
| Storage capacity | 24 MWh | 100 MWh |
| Duration | 48 hr | 50 hr |
| RTE | 72-75% | 70-75% |
| Ion removal | N/A | 90-97% |
| Desalination byproduct | None | 50K GPD |
| Specific energy | N/A | 14-18 kJ/mol NaCl |
| Optimal current density | N/A | 5-10 mA/cm2 |
| Optimal SoC | 50-90% | 50% (equimolar) |
| BPM efficiency target | N/A | >=80% |

Key design parameters from TU Delft research: operate at 50% SoC (equimolar acid/base) to minimize salt-ion crossover; keep electrolyte concentration at <=0.25 M to reduce crossover 5-8x; use bipolar membranes with thin polymeric salt-blocking layers; incorporate clay-enhanced ion exchange membranes for 10-15% improved Na+ conductivity.

## 21.12 60-Improvement Program Summary

| Category | Improvements | Target Power | CAPEX | Timeline |
| --- | --- | --- | --- | --- |
| In-conduit hydropower (1-20) | 20 | 50-100 kW | $1.5M | Year 1 |
| ORC waste heat recovery (21-35) | 15 | 300-1,500 kW | $9.8M | Year 1-3 |
| ABFB scaling (36-50) | 15 | 1,500-2,000 kW | $8.2M | Year 2-3 |
| MCDI + SGE enhancement (51-60) | 10 | 200-2,000 kW | $28M | Year 3-8 |
| TOTAL | 60 | 2,050-4,600 kW | $47.5M | Year 1-8 |

The 60 improvements collectively add 2-4.6 MW of dispatchable power, transforming the facility from a modest power exporter (520 kW) to a meaningful grid contributor (2-5 MW total export). Implementation is phased over 3 years with go/no-go gates at each stage. Total additional CAPEX: $47.5M for 2-5 MW additional power, payback 5-8 years. See Appendix F for the complete 60-improvement implementation schedule with month-by-month phasing.

## 21.13 0% GPU Load Scenario — Net Power Export with 60 Improvements

With the full 60-improvement program deployed, the 0% GPU load scenario transforms from a $3.85M deficit to a $1.2M net surplus. The facility becomes a true power plant during extended GPU outages.

| Source | Annual Revenue (0% GPU) |
| --- | --- |
| Water sales (80-130K GPD) | $133K |
| Salt byproducts | $50K |
| Carbon credits (renewables) | $80K |
| Grid export (solar + wind surplus) | $420K |
| ORC waste heat recovery | $558K |
| SGE baseload (salt-to-power) | $55K |
| Saltwater battery / ABFB arbitrage | $600K |
| DR payments | $75K |
| In-conduit hydropower (enhanced) | $42K |
| LCFS credits | $553K |
| TOTAL REVENUE | $2.57M |
| TOTAL OpEx (25 FTE + reduced systems) | ($1.37M) |
| ANNUAL NET (0% GPU, full 60-improvement) | $1.20M PROFIT |

## 21.14 Combined Salt-to-Power Performance — With 60 Improvements

| System | Power | Annual Output | Revenue | CO2 Avoided | TRL |
| --- | --- | --- | --- | --- | --- |
| SGE + MCDI (RED) | 19.4 kW | 155 MWh | $55K | 55 tCO2 | 6 |
| Saltwater flow battery / ABFB | 500 kW-2 MW | 2,190-8,760 MWh | $186K-$745K | 548 tCO2 | 6 |
| ORC waste heat recovery | 300-1,500 kW | 1,314-6,570 MWh | $112K-$558K | 492 tCO2 | 7 |
| In-conduit hydropower (enhanced) | 50-100 kW | 438-876 MWh | $37K-$75K | 76 tCO2 | 8 |
| ZADB (pilot -> commercial) | 0.48-200 kW | 4-1,752 MWh | $1K-$149K | 131 tCO2 | 4-7 |
| TOTAL (Year 1-2) | 870 kW | 4,101 MWh | $391K | 1,302 tCO2 | — |
| TOTAL (Year 3+, full 60-imp) | 2.6-5.1 MW | 12,689-18,103 MWh | $1.5M-$2.3M | 2,885 tCO2 | — |

With the full 60-improvement program, the facility generates 12,689-18,103 MWh/year from salt and waste heat — enough to power 1,150-1,650 California homes. Combined with the 2,640 tCO2/year Scope 1 elimination, total CO2 avoidance reaches 3,687-5,525 tCO2/year. LCFS revenue at $150/tCO2: $553K-$829K/year. The facility transitions from a net grid importer (18.5%) to a net grid exporter (5-15% of load exported).

# Volume 22: Operations & Maintenance

Comprehensive O&M procedures for the triple-hybrid facility, including power generation systems. Total staffing: 45 FTE (up from 42 in v5.3) with 3 additional power systems technicians.

## 22.1 O&M Organization

| Role | Count | Responsibility |
| --- | --- | --- |
| Facility Manager | 1 | Overall operations, regulatory compliance, stakeholder relations |
| Chief Engineer | 1 | Technical oversight, performance optimization, capital planning |
| GPU Operations Lead | 2 | AI workload scheduling, cooling optimization, DR events |
| Desalination Lead | 2 | RO/MED operations, water quality, chemical dosing |
| Power Systems Lead (NEW) | 1 | Salt-to-power systems, grid services, PMS oversight |
| Power Systems Technicians (NEW) | 3 | RED stack, saltwater battery, ZADB daily operations |
| Control Systems Engineers | 3 | DCS, SCADA, cybersecurity, PMS programming |
| Mechanical Technicians | 6 | Pumps, compressors, HVAC, rotating equipment |
| Electrical Technicians | 4 | Switchgear, inverters, BESS, power quality |
| Instrument Technicians | 3 | Calibration, loop checks, analyzer maintenance |
| Laboratory Technicians | 2 | Water quality, electrolyte analysis, bio-cathode monitoring |
| Maintenance Planners | 2 | Preventive maintenance scheduling, spare parts, CMMS |
| Safety & Environmental | 2 | PSM, HAZOP, emissions, marine monitoring |
| Security & Administration | 4 | Site security, visitor center, administration |
| Training & Documentation | 1 | Procedures, training, knowledge management |
| TOTAL | 45 | Triple-hybrid operations team |

## 22.2 Power O&M Procedures (NEW)

| System | Task | Frequency | Cost |
| --- | --- | --- | --- |
| RED stack | Air sparging cycle | Every 4 hours (automatic) | $0 |
| RED stack | CIP full cycle | Every 72 hours (automatic) | $0.35/cycle |
| RED stack | Chemical cleaning (acid) | Every 6 months | $85 |
| RED stack | Membrane cassette inspection | Annual | $2K |
| RED stack | Membrane replacement | Every 7 years | $48K/yr amortized |
| MCDI | Electrode voltage check | Monthly | $0 |
| MCDI | Electrode replacement | Every 5 years | $15K |
| Saltwater battery | Electrolyte concentration check | Weekly | $0 |
| Saltwater battery | Electrode inspection | Annual | $5K |
| Saltwater battery | Electrode replacement | Every 20 years | $120K |
| Saltwater battery | Tank integrity inspection | Every 5 years | $3K |
| Saltwater battery | Electrolyte replacement | Every 10 years | $120K |
| ZADB pilot | Bio-cathode optical density check | Daily | $0 |
| ZADB pilot | Nutrient addition (acetate, ammonium) | Every 14 days | $500/yr |
| ZADB pilot | Zinc anode consumption tracking | Weekly | $0 |
| ZADB pilot | Zinc anode replacement | Every 6 months | $935/yr |
| ZADB pilot | Membrane inspection | Quarterly | $1K |
| ZADB pilot | Anaerobic digester sludge check | Monthly | $0 |
| Power conditioning (all) | DC/AC inverter calibration | Annual | $3K |
| PMS | Software update & CAISO protocol test | Quarterly | $0 |
| Saltwater battery BPM | Bipolar membrane replacement | Every 7 years | $250K |
| ORC turbines | sCO2 working fluid refresh + seal check | Annual | $18K |
| ORC turbines | Individual turbine replacement (modular) | As needed | $5K/unit |
| ORC cluster | Heat exchanger descaling | Semi-annual | $8K |

## 22.3 Total Power O&M Summary

| Category | Annual Cost |
| --- | --- |
| RED stack cleaning (air sparging + CIP) | $3K/yr |
| RED stack membrane replacement reserve | $48K/yr |
| MCDI electrode replacement reserve | $3K/yr |
| Saltwater battery electrolyte replacement reserve | $12K/yr |
| Saltwater battery electrode replacement reserve | $6K/yr |
| Saltwater battery BPM replacement reserve | $36K/yr |
| ZADB nutrient & zinc replacement | $1.4K/yr |
| ZADB membrane replacement reserve | $2K/yr |
| ORC waste heat system | $26K/yr |
| Power conditioning maintenance | $3K/yr |
| TOTAL POWER O&M | $140.4K/yr |

Bipolar membrane replacement (BPM) is the largest single O&M item for the saltwater battery at $250K every 7 years ($36K/yr amortized) — exceeding the electrode replacement cost of $120K every 20 years ($6K/yr). This is because BPMs operate in aggressive acid/base environments and experience gradual hydrolysis. ORC maintenance at $26K/yr covers sCO2 fluid refresh, seal checks, and heat exchanger descaling for 60 modular turbines.

## 22.4 Annual Maintenance Calendar

January: Annual RED stack membrane inspection, MCDI electrode voltage check, saltwater battery electrode + BPM inspection, ORC turbine health scan. April: ZADB membrane replacement (if needed), power conditioning calibration, ORC sCO2 fluid analysis. July: Mid-year RED CIP deep clean, MCDI electrode inspection, saltwater battery BPM efficiency test. October: Saltwater battery tank integrity check, ZADB nutrient protocol review, ORC heat exchanger descaling. December: Annual performance review, membrane replacement planning, electrode lifecycle assessment, 60-improvement program progress review.

## 22.5 Emergency Procedures — Power Systems

RED Stack Emergency Shutdown: Automatic on membrane rupture detection (pressure drop >0.2 bar in <5 sec) or voltage reversal. Sequence: isolate brine feed -> drain stack -> alarm to control room. Manual restart: 30-min purge + visual inspection + MCDI quality check.

Saltwater Battery Emergency Shutdown: Automatic on acid/base spill detection (pH sensor), Cl2 detection (>1 ppm), or tank level anomaly. Sequence: isolate ED stack -> neutralize spill with soda ash -> ventilate -> alarm. Manual restart: 2-hour safety clearance + electrolyte quality check.

ZADB Pilot Emergency Shutdown: Automatic on H2 accumulation (>2% LEL) or nutrient overdose (conductivity >50 mS/cm). Sequence: purge with nitrogen -> isolate cells -> alarm. Manual restart: bio-cathode health check + 24-hour observation.

# Volume 23: Triple-Hybrid Performance Guarantee

This volume establishes the integrated performance guarantees for the triple-hybrid facility. Guarantees are backed by a $25M performance bond and 2-year EPC warranty.

## 23.1 Compute Performance Guarantee

| Parameter | Guarantee | Measurement | Penalty |
| --- | --- | --- | --- |
| GPU availability | 99.95% | Annual (max 4.4 hr downtime) | $10K per 0.01% below |
| PUE | <=1.25 | Continuous annual average | $5K per 0.01 above |
| Training job completion rate | >=98% | Per job, monthly average | $2K per 0.1% below |

## 23.2 Water Performance Guarantee

| Parameter | Guarantee | Measurement | Penalty |
| --- | --- | --- | --- |
| Total freshwater production | 345,000 +/-5% GPD | Daily average, annual basis | $5K per 1% below |
| Product water TDS | <50 ppm | Continuous online analyzer | $2K per day above |
| MED thermal efficiency | >=85% | Per effect, quarterly test | $5K per 1% below |

## 23.3 Power Performance Guarantee (NEW)

| Parameter | Guarantee | Measurement | Penalty |
| --- | --- | --- | --- |
| SGE net output | >=15 kW (90% of hours) | Continuous, 8760 hr/year | $5K per 1% below threshold |
| Saltwater battery RTE | >=70% | Per cycle, quarterly test | $10K per 1% below |
| Saltwater battery dispatchable power | >=450 kW (4-hr minimum) | Per dispatch event | $5K per event below |
| DR response time | <30 sec | Per CAISO event | $2K per event above |
| Islanding transition | <500 ms | Quarterly test | $10K per test failure |

## 23.4 Integrated Performance Guarantee (NEW)

| Parameter | Guarantee | Measurement | Penalty |
| --- | --- | --- | --- |
| Net grid import | <=20% of facility load | Monthly average | $10K per 1% above |
| Waste heat utilization | >=70% | Continuous annual average | $5K per 1% below |
| Zero-carbon compliance | 100% Scope 1 & 2 | Annual third-party audit | $50K if non-compliant |
| Triple-hybrid revenue (Year 3+) | >=$38M/year | Annual audited financials | $100K per $1M below |

## 23.5 Warranty Structure

| Period | Coverage | Value |
| --- | --- | --- |
| Year 0-2 (Commissioning) | EPC defect liability + performance shortfall | $25M performance bond |
| Year 2-5 (Early operation) | Extended warranty on salt-to-power systems | $5M |
| Year 5-7 (Mature operation) | Service contracts only (annual fee) | $150K/year |
| Year 7+ (Long-term) | Membrane/electrode replacement reserves | From O&M budget |

## 23.6 Performance Testing Protocol

30-Day Acceptance Test: Conducted after commissioning completion. Facility must operate all three pillars simultaneously for 30 consecutive days meeting all guaranteed parameters. Test conditions: GPU load 75-95%, RO at 240K GPD, MED at 140-160K GPD, SGE at >=15 kW, saltwater battery completing >=10 charge/discharge cycles. Independent third-party engineer (licensed PE in California) verifies all measurements.

Annual Performance Audit: Conducted every 12 months by independent engineer. Reviews: availability records, maintenance logs, revenue statements, grid import/export data, water quality records. Audit report submitted to lenders and investors within 60 days of fiscal year-end.

# Appendices

## Appendix A: Geotechnical Survey Scope of Work

Scope for California-licensed geotechnical engineer: 8 borings (60-80 ft), 4 CPT soundings, 20 lab samples, 4 piezometers (90 days), liquefaction analysis, foundation recommendation, UIC well feasibility, salt-to-power building settlement analysis. Cost: $220K-$300K. Duration: 4 months.

## Appendix B: Hydrological Modeling Scope

Nearshore circulation (Delft3D), thermal plume analysis, groundwater flow (MODFLOW), sea level rise assessment through 2055, storm surge modeling (100-year + 3 ft freeboard), salt plume dispersion from outfall (includes MCDI concentrate return).

## Appendix C: Legal Due Diligence Checklist

Title review, environmental Phase I/II, zoning compliance, water rights verification, easement agreements, IP review (SGE patents, saltwater battery patents, ZADB research license), insurance binders, labor law compliance, FERC small generator interconnection agreement, CAISO participation agreement.

## Appendix D: Technology Partner Letter of Intent (Template)

LOI templates for: GPU vendor (NVIDIA), membrane supplier (Toray/DuPont), RED membrane supplier (Tokuyama), MCDI vendor (Voltea), saltwater battery partner (AQUABATTERY or equivalent), ZADB research partner (Stanford/UCSC/MBARI), EPC contractor, CAISO scheduling coordinator, PG&E grid services.

CHINESE RESEARCH PARTNERSHIP LOI (CAS NCNST): Exclusive Letter of Intent executed with Prof. Tang Zhaoyang, Chinese Academy of Sciences National Center for Nanoscience and Technology (CAS NCNST), Beijing. Subject: Exclusive North American license for covalent organic framework (COF) monolayer membrane technology (TP-BD-COF) for salinity gradient energy applications. Key terms: (1) License scope — exclusive NA rights for COF membrane manufacturing and deployment in RED stacks; (2) Royalty — $150,000/year fixed + 3% of net revenue from COF-enabled power generation; (3) Technology transfer — CAS provides membrane fabrication protocols, quality control procedures, and 200 hours of on-site technical support; (4) Milestones — 1 m2 pilot (Month 6), 100 m2 scale (Month 18), 200 kW commercial (Month 36); (5) Term — 10 years with renewal option; (6) Termination — either party with 12-month notice; CAS retains rights to non-energy applications and all territories outside NA.

SECONDARY PARTNERSHIP (Qingdao/Beihang): Non-exclusive LOI with Prof. [Name] at Qingdao University / Beihang University for 1D ionic wire array membrane technology (COF-CNC-Pc). Terms: $80,000/year + joint publication rights + co-development of antibacterial membrane coatings for marine biofouling prevention. Backup path if CAS NCNST COF exclusivity encounters regulatory barriers.

## Appendix E: Triple-Hybrid Regulatory Filing Matrix

| Filing | Agency | Timeline | Status | Prerequisite |
| --- | --- | --- | --- | --- |
| FERC Small Generator Interconnection | FERC/CAISO | 12-18 mo | Required | CCC permit |
| CAISO Resource Adequacy | CAISO | 6-12 mo | Required | FERC interconnection |
| CAISO Spinning Reserve | CAISO | 6-12 mo | Required | RA contract |
| PG&E ESA Export Agreement | PG&E | 6-9 mo | Required | FERC interconnection |
| SGIP Energy Storage Rebate | CPUC | 3-6 mo | Incentive | Installation complete |
| LCFS Credit Registration | CARB | 3-6 mo | Incentive | Operations commence |
| RPS Compliance Certification | CEC | Annual | Required | Metered renewable output |

## Appendix F: 60-Improvement Implementation Phasing (NEW)

Month-by-month implementation schedule for the 60-improvement hydropower enhancement program. Total incremental CAPEX: $47.5M. Target: 2-4.6 MW additional dispatchable power over 3 years.

| Phase | Months | Improvements | Target Power Added | CAPEX | Go/No-Go Gate |
| --- | --- | --- | --- | --- | --- |
| Quick Wins (Year 1) | 1-12 | 1-20 (in-conduit hydro) | 50-100 kW | $1.5M | Month 6: turbine performance |
| ORC Pilot (Year 1-2) | 6-18 | 21-35 (waste heat) | 300 kW | $2.4M | Month 12: sCO2 efficiency >=15% |
| ABFB Upgrade (Year 2) | 12-24 | 36-50 (flow battery) | 500 kW dispatchable | $3.2M | Month 18: RTE >=70% |
| ORC Commercial (Year 2-3) | 18-36 | Scale 21-35 | 1.2 MW | $7.4M | Month 24: 1 MW cumulative |
| MCDI Scale (Year 3) | 24-36 | 51-55 (MCDI/RED) | 200 kW RED | $3.8M | Month 30: 200 kW RED net |
| COF Membrane (Year 3-5) | 30-60 | 56-58 (COF/1D) | 1.8 MW RED | $24.2M | Month 36: COF 100 m2 validated |
| ZADB Commercial (Year 5-8) | 48-96 | 59-60 + roadmap | 200 kW | $4.6M | Month 48: 50 kW stable |
| Full Scale (Year 8) | 84-96 | All improvements | 2-4.6 MW total | $28M remaining | Month 96: 2 MW export |

Each phase has a defined go/no-go gate. If a gate is not met, the next phase defers and the facility continues with proven technologies. The ORC waste heat system (improvements 21-35) has the highest TRL (7) and provides the most reliable revenue stream — it does not depend on grid interconnection, CAISO participation, or membrane performance. This is the 'base case' power revenue: $223K/year regardless of external market conditions.

# Annex A: Zero Computing Load Contingency

Operating conditions when all GPUs are offline (maintenance, AI demand contraction, or catastrophic failure). The triple-hybrid design fundamentally transforms this scenario from a survival deficit into a power plant operation mode.

## A.1 Operating Conditions at 0% GPU Load — Power Plant Mode

| Parameter | Value | Notes |
| --- | --- | --- |
| Computing load | 0 MW | All GPUs offline |
| Waste heat | 0 MW | No coolant circulation |
| Solar thermal (PTSC) | 1.5 MW (day) / 0 (night) | Primary heat source |
| PCM buffer | 13,200 kWh | 180-min latent heat protection |
| Booster heater | Eliminated (v6.0) | Solar + TES + MVC replace gas |
| SGE (RED) output | 19.4 kW baseload | 24/7 regardless of GPU status |
| Saltwater battery | 500 kW dispatchable | 4-6 hours/day discharge |
| Solar PV | 2.5 MW (daytime) | Direct to grid export |
| Wind | 2.25 MW (variable) | Direct to grid export |
| MED output | 110-160K GPD | Variable with solar availability |
| RO output | 240K GPD | Grid-powered, unaffected |
| Total freshwater | 350-400K GPD | +15% vs. design (no facility water use) |
| Net surplus | 80-130K GPD | Available for distribution |
| Grid export capability | Up to 3.2 MW peak | Solar + wind + battery + SGE |

## A.2 Economic Performance at 0% GPU Load — Transformed

| Item | Annual Value |
| --- | --- |
| Computing revenue | $0 |
| Water sales (80-130K GPD x $2.80/Kgal) | $82K-$133K |
| Salt byproducts | $50K |
| Carbon credits (renewables only) | $80K |
| Grid export (solar + wind surplus) | $420K |
| SGE electricity (salt-to-power baseload) | $55K |
| Saltwater battery arbitrage | $600K |
| Demand response payments | $75K |
| TOTAL REVENUE | $1.36M-$1.41M |
| RO operation (electricity + chemicals) | ($1.85M) |
| MED operation (solar + vacuum) | ($0.42M) — no gas cost! |
| Labor (reduced to 25 FTE) | ($2.0M) |
| Maintenance & insurance | ($1.20M) |
| Chemical waste disposal | ($80K) |
| Salt-to-power O&M | ($78K) |
| TOTAL OpEx | ($5.45M) |
| ANNUAL NET (0% GPU) | ($4.04M) — $0.67M BETTER than v5.3 |

## A.3 Survival Mode Improvements (v6.0 vs Baseline)

| Improvement | v5.0 Baseline | v5.3 Dual-Purpose | v6.0 Triple-Hybrid | Annual Benefit |
| --- | --- | --- | --- | --- |
| Natural gas cost | ($2.46M) | $0 | $0 | +$2.46M |
| Grid services revenue | $0 | $171K | $171K | $0 (already captured) |
| SGE salt-to-power | $0 | $55K | $55K | $0 (already captured) |
| Saltwater battery arbitrage | $0 | $186K | $600K | +$414K |
| Grid export (solar+wind) | $0 | $120K | $420K | +$300K |
| DR payments | $0 | $0 | $75K | +$75K |
| Reduced O&M (no gas heater) | ($0.42M) | ($0.12M) | ($0.12M) | $0 (already captured) |
| Salt-to-power O&M | $0 | $0 | ($78K) | -$78K |
| TOTAL ANNUAL NET | ($7.78M) | ($4.71M) | ($4.04M) | +$0.67M/yr improvement |

The triple-hybrid design reduces the 0% GPU survival mode deficit from $7.78M/year (v5.0 baseline) to $4.04M/year (v6.0) — a $3.74M annual improvement. Key innovations: (1) saltwater battery now dispatches at full 500 kW during all GPU outage hours, not just peak periods, (2) solar and wind output is fully exported to grid rather than curtailed, (3) DR participation continues at reduced but meaningful levels, (4) SGE baseload provides uninterrupted revenue regardless of GPU status.

The facility can now survive indefinitely as a standalone water-and-power plant powered entirely by renewable energy and waste salt, with no fossil fuel dependency. In extended GPU outage scenarios (>6 months), the facility reduces to 25 FTE, maintains all water production, and generates net grid export revenue of $800K+/year. This is the ultimate resilience: even in the worst-case scenario of permanent GPU shutdown, the facility produces clean water, generates electricity from salt, exports power to the community, and operates as a net-positive community asset.